## Protocol Explanation
Write Format
Device Address | Function Code | Start Address |  | Write Register No. |  | Write Byte No. | Data to write in |  |  |  |  | CRC
1 Byte | 1 Byte | Hi Byte | Low Byte | Hi Byte | Low Byte | 1 Byte | Hi Byte 1 | Low Byte 1 | … | Hi Byte N | Low Byte N | Low Byte | Hi Byte
Broadcast Address:0x00; Device Address:1-247 | Write Function Code:0x10 | [5 empty] | For 32bits or 64bit data, it will be sent by Big-endian mode if there is no special explanation. For example, sequence to send a 32bits data: byte3, byte2, byte1, byte0 |  |  |  |  | Modbus-CRC16
Response Format of Write
Device Address | Function Code | Start Address |  | Write Register No. |  | CRC
1 Byte | 1 Byte | Hi Byte | Low Byte | Hi Byte | Low Byte | Low Byte | Hi Byte
Slave Address | Write Function Code:0x10 |  |  |  |  | Modbus-CRC16
Read Format
Device Address | Function Code | Start Address |  | Read Register No. |  | CRC
1 Byte | 1 Byte | Hi Byte | Low Byte | Hi Byte | Low Byte | Low Byte | Hi Byte
Device Address:1-247 | ReadFunction Code:0x03 |  |  |  |  | Modbus-CRC16
Response Format of Read
Device Address | Function Code | Data Byte No. | Response register data |  |  |  |  | CRC
1 Byte | 1 Byte | 1 Byte | Hi Byte 1 | Low Byte 1 | … | Hi Byte N | Low Byte N | Low Byte | Hi Byte
Slave Address | ReadFunction Code:0x03 |  | For 32bits or 64bit data, it will be sent by Big-endian mode if there is no special explaination. For example , sequence to send a 32bits data: byte3,byte2,byte1,byte0 |  |  |  |  | Modbus-CRC16
Abnormal Response
Device Address | Function Code | Error Code |  | CRC
1 Byte | 1 Byte | 1 Byte |  | Low Byte | Hi Byte
Slave Address | Abnormal Function Code:0x90 | See Error Code List |  | Modbus-CRC16
Read and write explanation
Value | Name | Explanation
R | Readable | Readable registers
W | Writable | Writable registers
V | Volatile | Variable registers, support frequent write operations

## Registers
Register address (Dec) | Register address (Hex) | Campo | Type | Precision | Unit | Min | Max | Read/Write | Remarks | User
General
64 | 0040 | AddressMask_General1 | U64 |  |  |  |  | R | The validity of 64 addresses above the address range (including the address of this partition) corresponding to each bit of this partition. 0 means invalid; 1 means valid. | End User
65 | 0041 | [8 empty] | End User
66 | 0042 | [8 empty] | End User
67 | 0043 | [8 empty] | End User
68 | 0044 | Modbus_Protocol_Version | BCD16 |  |  | 1.06 | 99.99 | R | Version number of this protocol. The protocol version number corresponds to the version number in the cover of this protocol. Bits 0-7 represent the minor version number, bits 0-3 represent the low version number, and bits 4-7 represent the high version number. Bits 8-15 represent the major version number, of which bits 8-11 represent the low-order version number, and bits 12-15 represent the high-order version number. Example: The value 0x1234 indicates that the protocol version number is 12.34 | End User
69 | 0045 | COMM_MCU_Code | ASCII |  |  |  |  | R | Communication chip code. Refer to the chip coding specification, not open to modify. Example: 0x4730 means "G0" | End User
70 | 0046 | CTRL1_MCU_Code | ASCII |  |  |  |  | R | No. 1 control chip code. Refer to the chip coding specification, not open to Modify. Example: 0x4730 means "G0" | End User
71 | 0047 | CTRL2_MCU_Code | ASCII |  |  |  |  | R | No. 2 control chip code name. Refer to the chip coding specification, not open to Modify. Example: 0x4730 means "G0" | End User
72 | 0048 | MCU_Code_Rsvd1
73 | 0049 | MCU_Code_Rsvd2
74 | 004A | MCU_Code_Rsvd3
75 | 004B | MCU_Code_Rsvd4
76 | 004C | MCU_Code_Rsvd5
77 | 004D | MCU_Code_Rsvd6
78 | 004E | MCU_Code_Rsvd7
79 | 004F | MCU_Code_Rsvd8
80 | 0050 | MCU_Code_Rsvd9
81 | 0051 | MCU_Code_Rsvd10
82 | 0052 | MCU_Code_Rsvd11
83 | 0053 | MCU_Code_Rsvd12
84 | 0054 | MCU_Code_Rsvd13
85 | 0055
86 | 0056
87 | 0057
88 | 0058
89 | 0059
90 | 005A
91 | 005B
92 | 005C
93 | 005D
94 | 005E
95 | 005F
96 | 0060
97 | 0061
98 | 0062
99 | 0063
100 | 0064
101 | 0065
102 | 0066
103 | 0067
104 | 0068
105 | 0069
106 | 006A
107 | 006B
108 | 006C
109 | 006D
110 | 006E
111 | 006F
112 | 0070
113 | 0071
114 | 0072
115 | 0073
116 | 0074
117 | 0075
118 | 0076
119 | 0077
120 | 0078
121 | 0079
122 | 007A
123 | 007B
124 | 007C
125 | 007D
126 | 007E
127 | 007F
0
Real time data (0x0400-0x07FF)
System info (0x0400-0x047F)
1024 | 0400 | AddressMask_Realtime_SysInfo1 | U64 |  |  |  |  | R | The validity of 64 addresses above the address range (including the address of this partition) corresponding to each bit of this partition. 0 means invalid; 1 means valid. | End User
1025 | 0401 | [8 empty] | End User
1026 | 0402 | [8 empty] | End User
1027 | 0403 | [8 empty] | End User
1028 | 0404 | SysState | U16 |  |  |  |  | R | Operating status 0: waiting state 1: Detection status 2: Grid-connected status 3: Emergency power supply status 4: Recoverable fault state 5: Permanent fault status 6: Upgrade status 7: Self-charging status | End User
1029 | 0405 | Fault1 | U16 |  |  |  |  | R | Fault information table 1 | End User
1030 | 0406 | Fault2 | U16 |  |  |  |  | R | Fault information table 2 | End User
1031 | 0407 | Fault3 | U16 |  |  |  |  | R | Fault information table 3 | End User
1032 | 0408 | Fault4 | U16 |  |  |  |  | R | Fault information table 4 | End User
1033 | 0409 | Fault5 | U16 |  |  |  |  | R | Fault information table 5 | End User
1034 | 040A | Fault6 | U16 |  |  |  |  | R | Fault information table 6 | End User
1035 | 040B | Fault7 | U16 |  |  |  |  | R | Fault information table 7 | End User
1036 | 040C | Fault8 | U16 |  |  |  |  | R | Fault information table 8 | End User
1037 | 040D | Fault9 | U16 |  |  |  |  | R | Fault information table 9 | End User
1038 | 040E | Fault10 | U16 |  |  |  |  | R | Fault information table 10 | End User
1039 | 040F | Fault11 | U16 |  |  |  |  | R | Fault information table 11 | End User
1040 | 0410 | Fault12 | U16 |  |  |  |  | R | Fault information table 12 | End User
1041 | 0411 | Fault13 | U16 |  |  |  |  | R | Fault information table 13 | End User
1042 | 0412 | Fault14 | U16 |  |  |  |  | R | Fault information table 14 | End User
1043 | 0413 | Fault15 | U16 |  |  |  |  | R | Fault information table 15 | End User
1044 | 0414 | Fault16 | U16 |  |  |  |  | R | Fault information table 16 | End User
1045 | 0415 | Fault17 | U16 |  |  |  |  | R | Fault information table 17 | End User
1046 | 0416 | Fault18 | U16 |  |  |  |  | R | Fault information table 18 | End User
1047 | 0417 | Countdown | U16 | 1 | seconds |  |  | R | Power-on countdown | End User
1048 | 0418 | Temperature_Env1 | I16 | 1 | ℃ |  |  | R | Ambient temperature 1 | End User
1049 | 0419 | Temperature_Env2 | I16 | 1 | ℃ |  |  | R | Ambient temperature 2 | End User
1050 | 041A | Temperature_HeatSink1 | I16 | 1 | ℃ |  |  | R | Radiator temperature 1 | End User
1051 | 041B | Temperature_HeatSink2 | I16 | 1 | ℃ |  |  | R | Radiator temperature 2 | End User
1052 | 041C | Temperature_HeatSink3 | I16 | 1 | ℃ |  |  | R | Radiator temperature 3 | End User
1053 | 041D | Temperature_HeatSink4 | I16 | 1 | ℃ |  |  | R | Radiator temperature 4 | End User
1054 | 041E | Temperature_HeatSink5 | I16 | 1 | ℃ |  |  | R | Radiator temperature 5 | End User
1055 | 041F | Temperature_HeatSink6 | I16 | 1 | ℃ |  |  | R | Radiator temperature 6 | End User
1056 | 0420 | Temperature_Inv1 | I16 | 1 | ℃ |  |  | R | Module temperature 1 | End User
1057 | 0421 | Temperature_Inv2 | I16 | 1 | ℃ |  |  | R | Module temperature 2 | End User
1058 | 0422 | Temperature_Inv3 | I16 | 1 | ℃ |  |  | R | Module temperature 3 | End User
1059 | 0423 | Temp_Rsvd1 | I16 | 1 | ℃ |  |  | R | Reserve temperature 1 | End User
1060 | 0424 | Temp_Rsvd2 | I16 | 1 | ℃ |  |  | R | Reserve temperature 2 | End User
1061 | 0425 | Temp_Rsvd3 | I16 | 1 | ℃ |  |  | R | Reserve temperature 3 | End User
1062 | 0426 | GenerationTime_Today | U16 | 1 | Minute |  |  | R | Day of power generation time | End User
1063 | 0427 | GenerationTime_Total | U32 | 1 | Minute |  |  | R | Total power generation time | End User
1064 | 0428
1065 | 0429 | ServiceTime_Total | U32 | 1 | Minute |  |  | R | Total running time | End User
1066 | 042A
1067 | 042B | InsulationResistance | U16 | 1 | kΩ |  |  | R | Insulation resistance | End User
1068 | 042C | SysTime_Year | U16 |  |  |  |  | R | System time-year | End User
1069 | 042D | SysTime_Month | U16 |  |  |  |  | R | System time-month | End User
1070 | 042E | SysTime_Date | U16 |  |  |  |  | R | System Time-Daily Minutes | End User
1071 | 042F | SysTime_Hour | U16 |  |  |  |  | R | System time-hour | End User
1072 | 0430 | SysTime_Minute | U16 |  |  |  |  | R | System time-minutes | End User
1073 | 0431 | SysTime_Second | U16 |  |  |  |  | R | System time-second | End User
1074 | 0432 | Fault19 | U16 |  |  |  |  | R | Fault message table 19 | End User
1075 | 0433 | Fault20 | U16 |  |  |  |  | R | Fault information table 20 | End User
1076 | 0434 | Fault21 | U16 |  |  |  |  | R | Fault information table 21 | End User
1077 | 0435 | Fault22 | U16 |  |  |  |  | R | Fault information table 22 | End User
1078 | 0436 | Fault23 | U16 |  |  |  |  | R | Fault information table 23 | End User
1079 | 0437 | Fault24 | U16 |  |  |  |  | R | Fault message table 24 | End User
1080 | 0438 | Fault25 | U16 |  |  |  |  | R | Fault information table 25 | End User
1081 | 0439 | Fault26 | U16 |  |  |  |  | R | Fault message table 26 | End User
1082 | 043A | Fault27 | U16 |  |  |  |  | R | Fault information table 27 | End User
1083 | 043B
1084 | 043C
1085 | 043D
1086 | 043E
1087 | 043F
1088 | 0440 | AddressMask_Realtime_SysInfo2 | U64 |  |  |  |  | R | Each Character corresponds to the validity of 64 addresses in this field, . Bit4 represents the address where the highest bit address(Plus 1) of this field located 0 means invalid; 1 means valid. | End User
1089 | 0441 | [8 empty] | End User
1090 | 0442 | [8 empty] | End User
1091 | 0443 | [8 empty] | End User
1092 | 0444 | Production_Code | U16 | [5 empty] | Reversed
1093 | 0445 | Serial_Number0 | ASCII |  |  |  |  | R | The 1st and 2nd digits of the serial number. The High 8-bits store the 1st digit of Serial Number, The low 8-bits Store the 2nd digit of Serial number | End User
1094 | 0446 | Serial_Number1 | ASCII |  |  |  |  | R | The 3rd and 4th digits of the serial number. The High 8-bits store the 3rd digit of Serial Number, The low 8-bits Store the 4th digit of Serial number | End User
1095 | 0447 | Serial_Number2 | ASCII |  |  |  |  | R | The 5th and 6th digits of the serial number. The High 8-bits store the5th digit of Serial Number, The low 8-bit Store the 6th digit of Serial number | End User
1096 | 0448 | Serial_Number3 | ASCII |  |  |  |  | R | The 7th and 8th digits of the serial number. The High 8-bits store the 7th digit of Serial Number, The low 8-bits Store the 8th digit of Serial number | End User
1097 | 0449 | Serial_Number4 | ASCII |  |  |  |  | R | The 9th and 10th digits of the serial number. The High 8-bits store the 9th digit of Serial Number, The low 8-bits Store the 10th digit of Serial number | End User
1098 | 044A | Serial_Number5 | ASCII |  |  |  |  | R | The 11th and 12th digits of the serial number. The High 8-bits store the 11th digit of Serial Number, The low 8-bits Store the 12th digit of Serial number | End User
1099 | 044B | Serial_Number6 | ASCII |  |  |  |  | R | The 13th and 14th digits of the serial number. The High 8-bits store the 13th digit of Serial Number, The low 8-bits Store the 14th digit of Serial number | End User
1100 | 044C | Serial_Number7 | ASCII |  |  |  |  | R | The 15th and 16th digits of the serial number. The High 8-bits store the 15th digit of Serial Number, The low 8-bits Store the 16th digit of Serial number | End User
1101 | 044D | Hardware_Version0 | ASCII |  |  |  |  | R | The 1st and 2nd digits of the Hardware Version. The High 8-bits store the 1st digit of Serial Number, The low 8-bits Store the 2nd digit of Serial number | End User
1102 | 044E | Hardware_Version1 | ASCII |  |  |  |  | R | The 3rd and 4th digits of the Hardware Version. The High 8-bits store the 3rd digit of Serial Number, The low 8-bits Store the 4th digit of Serial number | End User
1103 | 044F | Software_Version_Stage_COM | ASCII |  |  |  |  | R | Bits for communication chip's software version number. The lower 8 bits of the register store the ASCII code. The default value of the official version is'V'. | End User
1104 | 0450 | Software_Version_Major_COM | ASCII |  |  |  |  | R | Software version number for Communication chip. For one system, the software version number need to be consistent for all chips. The high 8 bits of the register store the higher digits. The low 8 bits of the register store the lower digits. | End User
1105 | 0451 | Software_Version_Custom_COM | ASCII |  |  |  |  | R | Non-standard customization software version number for communication chip. The standard software version number should be"00",For one system, the Non-standard customization software version number need to be consistent for all chips, otherwise it will consider as "Fault". The high 8 bits of the register store the higher digits. The low 8 bits of the register store the lower digits. | End User
1106 | 0452 | Software_Version_Minor_COM | ASCII |  |  |  |  | R | Subversion software number for communication chip. The high 8 bits of the register store the higher digits; The low 8 bits of the register store the lower digits. | End User
1107 | 0453 | Software_Version_Stage_Master | ASCII |  |  |  |  | R | Bytes for main control chip's software version number, The lower 8 bits of the register store the ASCII code. The default value of the official version start with 'V'. The high 8 bits of the register store the higher digits; The low 8 bits of the register store the lower digits. | End User
1108 | 0454 | Software_Version_Major_Master | ASCII |  |  |  |  | R | Software version number for main control chip. For one system, the software version number need to be consistent for all chips. The high 8 bits of the register store the higher digits; The low 8 bits of the register store the lower digits. | End User
1109 | 0455 | Software_Version_Custom_Master | ASCII |  |  |  |  | R | Non-standard customization software version number for main control chip. The standard software version should be"00",For one system, the Non-standard customization software version number need to be consistent for all chips, otherwise it will consider as "Fault". The high 8 bits of the register store the higher digits; The low 8 bits of the register store the lower digits. | End User
1110 | 0456 | Software_Version_Minor_Master | ASCII |  |  |  |  | R | software subversion number for main control chip. The high 8 bits of the register store the higher digits; The low 8 bits of the register store the lower digits. | End User
1111 | 0457 | Software_Version_Stage_Slave | ASCII |  |  |  |  | R | Bits for Secondary control chip's software version number, The lower 8 bits of the register store the ASCII code. The default value of the official version is'V'.The high 8 bits of the register store the higher digits; The low 8 bits of the register store the lower digits. | End User
1112 | 0458 | Software_Version_Major_Slave | ASCII |  |  |  |  | R | Software version number for Secondary control chip. For one system, the software version number need to be consistent for all chips. The high 8 bits of the register store the higher digits; The low 8 bits of the register store the lower digits. | End User
1113 | 0459 | Software_Version_Custom_Slave | ASCII |  |  |  |  | R | Non-standard customization software version number for secondary control chip. The standard software version should be"00",For one system, the Non-standard customization software version number need to be consistent for all chips, otherwise it will consider as "Fault". The high 8 bits of the register store the higher digits; The low 8 bits of the register store the lower digits. | End User
1114 | 045A | Software_Version_Minor_Slave | ASCII |  |  |  |  | R | software subversion number for secondary control chip. The high 8 bits of the register store the higher digits; The low 8 bits of the register store the lower digits. | End User
1115 | 045B | Safety_Version_Major | U16 |  |  |  |  | R | main version number for Safety regulation library | End User
1116 | 045C | Safety_version_Minor | U16 |  |  |  |  | R | Sub-version number for Safety regulation library | End User
1117 | 045D | Boot_Version_COM | U16 |  |  |  |  | R |  | End User
1118 | 045E | Boot_Version_Master | U16 |  |  |  |  | R |  | End User
1119 | 045F | Boot_Version_Slave | U16 |  |  |  |  | R |  | End User
1120 | 0460 | Safety_Firmware_Version_Stage | ASCII |  |  |  |  | R | Safety certification software version number stage definition bit. The lower 8 bits of the register store the ASCII code. The default value of the official version is'V'. The high 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits. | End User
1121 | 0461 | Safety_Firmware_Version_Major | ASCII |  |  |  |  | R | The major version number of the safety certification software. The major version numbers of all chips in the same system must be the same, otherwise it will be regarded as a system failure. The high 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits. | End User
1122 | 0462 | Safety_Firmware_Version_Custom | ASCII |  |  |  |  | R | Safety certification software non-standard customized version number. The version number of the standard software is "00". The non-standard customized version numbers of all chips in the same system must be the same, otherwise it will be regarded as a system failure. The high 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits. | End User
1123 | 0463 | Safety_Firmware_Version_Minor | ASCII |  |  |  |  | R | Safety certification software version number. The high 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits. | End User
1124 | 0464 | Safety_Hardware_Version0 | ASCII |  |  |  |  | R | Safety certification hardware version number 1st and 2nd. The upper 8 bits of the register store the first bit of the serial number; The lower 8 bits of the register store the second bit of the serial number. | End User
1125 | 0465 | Safety_Hardware_Version1 | ASCII |  |  |  |  | R | The 3rd and 4th digits of the hardware version number of safety certification. The upper 8 bits of the register store the third bit of the serial number; The lower 8 bits of the register store the 4th bit of the serial number. | End User
1126 | 0466
1127 | 0467
1128 | 0468
1129 | 0469
1130 | 046A
1131 | 046B
1132 | 046C
1133 | 046D
1134 | 046E
1135 | 046F
1136 | 0470 | Serial_Number8 | ASCII |  |  |  |  | R | The 17th and 18th digits of the serial number. The upper 8 bits of the register store the 17th bit of the serial number; The lower 8 bits of the register store the 18th bit of the serial number. | End User
1137 | 0471 | Serial_Number9 | ASCII |  |  |  |  | R | The 19th and 20th digits of the serial number. The high 8 bits of the register store the 19th bit of the serial number; The lower 8 bits of the register store the 20th bit of the serial number. | End User
1138 | 0472 | Serial_Number11_Rsvd0 | ASCII |  |  |  |  | R
1139 | 0473 | Serial_Number11_Rsvd1 | ASCII |  |  |  |  | R
1140 | 0474 | Serial_Number12_Rsvd2 | ASCII |  |  |  |  | R
1141 | 0475 | Serial_Number13_Rsvd3 | ASCII |  |  |  |  | R
1142 | 0476 | Serial_Number14_Rsvd4 | ASCII |  |  |  |  | R
1143 | 0477
1144 | 0478
1145 | 0479
1146 | 047A
1147 | 047B
1148 | 047C
1149 | 047D
1150 | 047E
1151 | 047F
On grid output (0x0480-0x04FF)
1152 | 0480 | AddressMask_Realtime_GridOutput1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid. | End User
1153 | 0481
1154 | 0482
1155 | 0483
1156 | 0484 | Frequency_Grid | U16 | 0.01 | Hz |  |  | R | Grid frequency | End User
1157 | 0485 | ActivePower_Output_Total | I16 | 0.01 | kW |  |  | R | Total active power. Discharge is positive, charge is negative | End User
1158 | 0486 | ReactivePower_Output_Total | I16 | 0.01 | kW |  |  | R | Total reactive power. The inverter end is positive for leading and negative for lagging | End User
1159 | 0487 | ApparentPower_Output_Total | I16 | 0.01 | kW |  |  | R | Total apparent power. Discharge is positive, charge is negative | End User
1160 | 0488 | ActivePower_PCC_Total | I16 | 0.01 | kW |  |  | R | Total PCC active power. Selling electricity is positive, buying electricity is negative | End User
1161 | 0489 | ReactivePower_PCC_Total | I16 | 0.01 | kW |  |  | R | Total PCC reactive power. The inverter end is positive for lead and negative for lag | End User
1162 | 048A | ApparentPower_PCC_Total | I16 | 0.01 | kW |  |  | R | Total PCC apparent power. Selling electricity is positive, buying electricity is negative | End User
1163 | 048B | GridOutput_Rsvd1 | [5 empty] | R | Grid-connected output reserved 1 | End User
1164 | 048C | GridOutput_Rsvd2 | [5 empty] | R | Grid-connected output reserved 2 | End User
1165 | 048D | Voltage_Phase_R | U16 | 0.1 | V |  |  | R | R phase grid voltage | End User
1166 | 048E | Current_Output_R | U16 | 0.01 | A |  |  | R | R-phase inverter output current | End User
1167 | 048F | ActivePower_Output_R | I16 | 0.01 | kW |  |  | R | The R-phase inverter outputs active power. Discharge is positive, charge is negative | End User
1168 | 0490 | ReactivePower_Output_R | I16 | 0.01 | kW |  |  | R | The R-phase inverter outputs reactive power. The inverter end is positive for lead and negative for lag | End User
1169 | 0491 | PowerFactor_Output_R | I16 | 0.001 | p.u. |  |  | R | R-phase power factor. The inverter end is positive for lead and negative for lag | End User
1170 | 0492 | Current_PCC_R | U16 | 0.01 | A |  |  | R | R phase PCC current | End User
1171 | 0493 | ActivePower_PCC_R | I16 | 0.01 | kW |  |  | R | R-phase PCC active power | End User
1172 | 0494 | ReactivePower_PCC_R | I16 | 0.01 | kW |  |  | R | R-phase PCC reactive power. The inverter end is positive for lead and negative for lag | End User
1173 | 0495 | PowerFactor_PCC_R | I16 | 0.001 | p.u. |  |  | R | R-phase PCC power factor. The inverter end is positive for lead and negative for lag | End User
1174 | 0496 | R_Rsvd1 | [5 empty] | R | R phase reserved 1 | End User
1175 | 0497 | R_Rsvd2 | [5 empty] | R | R phase reserved 2 | End User
1176 | 0498 | Voltage_Phase_S | U16 | 0.1 | V |  |  | R | S phase grid voltage | End User
1177 | 0499 | Current_Output_S | U16 | 0.01 | A |  |  | R | S phase inverter output current | End User
1178 | 049A | ActivePower_Output_S | I16 | 0.01 | kW |  |  | R | The S-phase inverter outputs active power. Discharge is positive, charge is negative | End User
1179 | 049B | ReactivePower_Output_S | I16 | 0.01 | kW |  |  | R | The S-phase inverter outputs reactive power. The inverter end is positive for lead and negative for lag | End User
1180 | 049C | PowerFactor_Output_S | I16 | 0.001 | p.u. |  |  | R | S-phase power factor. The inverter end is positive for lead and negative for lag | End User
1181 | 049D | Current_PCC_S | U16 | 0.01 | A |  |  | R | S phase PCC current | End User
1182 | 049E | ActivePower_PCC_S | I16 | 0.01 | kW |  |  | R | S-phase PCC active power. Discharge is positive, charge is negative | End User
1183 | 049F | ReactivePower_PCC_S | I16 | 0.01 | kW |  |  | R | S-phase PCC reactive power. The inverter end is positive for lead and negative for lag | End User
1184 | 04A0 | PowerFactor_PCC_S | I16 | 0.001 | p.u. |  |  | R | S-phase PCC power factor. The inverter end is positive for lead and negative for lag | End User
1185 | 04A1 | S_Rsvd1 | [5 empty] | R | S phase reserved 1 | End User
1186 | 04A2 | S_Rsvd2 | [5 empty] | R | S phase reserved 2 | End User
1187 | 04A3 | Voltage_Phase_T | U16 | 0.1 | V |  |  | R | T phase grid voltage | End User
1188 | 04A4 | Current_Output_T | U16 | 0.01 | A |  |  | R | T-phase inverter output current | End User
1189 | 04A5 | ActivePower_Output_T | I16 | 0.01 | kW |  |  | R | The T-phase inverter outputs active power. Discharge is positive, charge is negative | End User
1190 | 04A6 | ReactivePower_Output_T | I16 | 0.01 | kW |  |  | R | The T-phase inverter outputs reactive power. The inverter end is positive for lead and negative for lag | End User
1191 | 04A7 | PowerFactor_Output_T | I16 | 0.001 | p.u. |  |  | R | T-phase power factor. The inverter end is positive for lead and negative for lag | End User
1192 | 04A8 | Current_PCC_T | U16 | 0.01 | A |  |  | R | T phase PCC current | End User
1193 | 04A9 | ActivePower_PCC_T | I16 | 0.01 | kW |  |  | R | T-phase PCC active power. Discharge is positive, charge is negative | End User
1194 | 04AA | ReactivePower_PCC_T | I16 | 0.01 | kW |  |  | R | T-phase PCC reactive power. The inverter end is positive for lead and negative for lag | End User
1195 | 04AB | PowerFactor_PCC_T | I16 | 0.001 | p.u. |  |  | R | T-phase PCC power factor. The inverter end is positive for lead and negative for lag | End User
1196 | 04AC | T_Rsvd1 | [5 empty] | R | T phase reserved 1 | End User
1197 | 04AD | T_Rsvd2 | [5 empty] | R | T phase reserved 2 | End User
1198 | 04AE | ActivePower_PV_Ext | U16 | 0.01 | kW |  |  | R | External power generation | End User
1199 | 04AF | ActivePower_Load_Sys | U16 | 0.01 | kW |  |  | R | System total load power | End User
1200 | 04B0 | Voltage_Phase_L1N | U16 | 0.1 | V |  |  | R | Grid L1 to N voltage effective value | End User
1201 | 04B1 | Current_Output_L1N | U16 | 0.01 | A |  |  | R | L1 output current effective value | End User
1202 | 04B2 | ActivePower_Output_L1N | I16 | 0.01 | kW |  |  | R | Active power output on L1 line | End User
1203 | 04B3 | Current_PCC_L1N | U16 | 0.01 | A |  |  | R | Effective value of CT current on L1 line | End User
1204 | 04B4 | ActivePower_PCC_L1N | I16 | 0.01 | kW |  |  | R | PCC active power on L1 line | End User
1205 | 04B5 | Voltage_Phase_L2N | U16 | 0.1 | V |  |  | R | Grid L2 to N voltage effective value | End User
1206 | 04B6 | Current_Output_L2N | U16 | 0.01 | A |  |  | R | L2 output current effective value | End User
1207 | 04B7 | ActivePower_Output_L2N | I16 | 0.01 | kW |  |  | R | Active power output on L2 line | End User
1208 | 04B8 | Current_PCC_L2N | U16 | 0.01 | A |  |  | R | Effective value of CT current on L2 line | End User
1209 | 04B9 | ActivePower_PCC_L2N | I16 | 0.01 | kW |  |  | R | Active power output on L2 line | End User
1210 | 04BA | Voltage_Line_L1 | U16 | 0.1 | V |  |  | R | L1 line voltage: voltage between R/S phase | End User
1211 | 04BB | Voltage_Line_L2 | U16 | 0.1 | V |  |  | R | L2 line voltage: voltage between S/T phase | End User
1212 | 04BC | Voltage_Line_L3 | U16 | 0.1 | V |  |  | R | L3 line voltage: voltage between T/R phase | End User
1213 | 04BD
1214 | 04BE
1215 | 04BF
1216 | 04C0
1217 | 04C1
1218 | 04C2
1219 | 04C3
1220 | 04C4
1221 | 04C5
1222 | 04C6
1223 | 04C7
1224 | 04C8
1225 | 04C9
1226 | 04CA
1227 | 04CB
1228 | 04CC
1229 | 04CD
1230 | 04CE
1231 | 04CF
1232 | 04D0
1233 | 04D1
1234 | 04D2
1235 | 04D3
1236 | 04D4
1237 | 04D5
1238 | 04D6
1239 | 04D7
1240 | 04D8
1241 | 04D9
1242 | 04DA
1243 | 04DB
1244 | 04DC
1245 | 04DD
1246 | 04DE
1247 | 04DF
1248 | 04E0
1249 | 04E1
1250 | 04E2
1251 | 04E3
1252 | 04E4
1253 | 04E5
1254 | 04E6
1255 | 04E7
1256 | 04E8
1257 | 04E9
1258 | 04EA
1259 | 04EB
1260 | 04EC
1261 | 04ED
1262 | 04EE
1263 | 04EF
1264 | 04F0
1265 | 04F1
1266 | 04F2
1267 | 04F3
1268 | 04F4
1269 | 04F5
1270 | 04F6
1271 | 04F7
1272 | 04F8
1273 | 04F9
1274 | 04FA
1275 | 04FB
1276 | 04FC
1277 | 04FD
1278 | 04FE
1279 | 04FF
Off grid output (0x0500-0x057F)
1280 | 0500 | AddressMask_Realtime_EmergencyOutput1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid | End User
1281 | 0501
1282 | 0502
1283 | 0503
1284 | 0504 | ActivePower_Load_Total | I16 | 0.01 | kW |  |  | R | Load active power. | End User
1285 | 0505 | ReactivePower_Load_Total | I16 | 0.01 | kW |  |  | R | Load consumption is positive, and feedback is negative | End User
1286 | 0506 | ApparentPower_Load_Total | I16 | 0.01 | kW |  |  | R | Load reactive power Apparent power of the load. Load consumption is positive, and feedback is negative | End User
1287 | 0507 | Frequency_Output | U16 | 0.01 | Hz |  |  | R | Output voltage frequency | End User
1288 | 0508 | ESOutput_Rsvd1 | [5 empty] | R | Off-grid total output reserved 1 | End User
1289 | 0509 | ESOutput_Rsvd2 | [5 empty] | R | Off-grid total output reserved 2 | End User
1290 | 050A | Voltage_Output_R | U16 | 0.1 | V |  |  | R | R-phase inverter output voltage | End User
1291 | 050B | Current_Load_R | I16 | 0.01 | A |  |  | R | R phase load current | End User
1292 | 050C | ActivePower_Load_R | I16 | 0.01 | kW |  |  | R | R-phase load active power. Load consumption is positive, and feedback is negative. | End User
1293 | 050D | ReactivePower_Load_R | I16 | 0.01 | kW |  |  | R | R-phase load reactive power. The inverter end is positive for lead and negative for lag | End User
1294 | 050E | ApparentPower_Load_R | I16 | 0.01 | kVA |  |  | R | Apparent power of R-phase load. Load consumption is positive, and feedback is negative. | End User
1295 | 050F | LoadPeakRatio_R | U16 | 0.01 | p.u. |  |  | R | R phase load peak ratio | End User
1296 | 0510 | ESR_Rsvd1 | [5 empty] | R | R phase reserved 1 | End User
1297 | 0511 | ESR_Rsvd2 | [5 empty] | R | R phase reserved 2 | End User
1298 | 0512 | Voltage_Output_S | U16 | 0.1 | V |  |  | R | S phase inverter output voltage | End User
1299 | 0513 | Current_Load_S | I16 | 0.01 | A |  |  | R | S phase load current | End User
1300 | 0514 | ActivePower_Load_S | I16 | 0.01 | kW |  |  | R | S-phase load active power. Load consumption is positive, and feedback is negative. | End User
1301 | 0515 | ReactivePower_Load_S | I16 | 0.01 | kW |  |  | R | S-phase load reactive power. The inverter end is positive for lead and negative for lag | End User
1302 | 0516 | ApparentPower_Load_S | I16 | 0.01 | kVA |  |  | R | Apparent power of S-phase load. Load consumption is positive, and feedback is negative. | End User
1303 | 0517 | LoadPeakRatio_S | U16 | 0.01 | p.u. |  |  | R | S phase load peak ratio | End User
1304 | 0518 | ESS_Rsvd1 | [5 empty] | R | S phase reserved 1 | End User
1305 | 0519 | ESS_Rsvd2 | [5 empty] | R | S phase reserved 2 | End User
1306 | 051A | Voltage_Output_T | U16 | 0.1 | V |  |  | R | T-phase inverter output voltage | End User
1307 | 051B | Current_Load_T | I16 | 0.01 | A |  |  | R | T phase load current | End User
1308 | 051C | ActivePower_Load_T | I16 | 0.01 | kW |  |  | R | T-phase load active power. Load consumption is positive, and feedback is negative. | End User
1309 | 051D | ReactivePower_Load_T | I16 | 0.01 | kW |  |  | R | T-phase load reactive power. The inverter end is positive for lead and negative for lag | End User
1310 | 051E | ApparentPower_Load_T | I16 | 0.01 | kVA |  |  | R | Apparent power of T-phase load. Load consumption is positive, and feedback is negative. | End User
1311 | 051F | LoadPeakRatio_T | U16 | 0.01 | p.u. |  |  | R | T-phase load peak ratio | End User
1312 | 0520 | EST_Rsvd1 | [5 empty] | R | T phase reserved 1 | End User
1313 | 0521 | EST_Rsvd2 | [5 empty] | R | T phase reserved 2 | End User
1314 | 0522 | Voltage_Output_L1N | U16 | 0.1 | V |  |  | R | Inverter L1 to N voltage effective value | End User
1315 | 0523 | Current_Load_L1N | I16 | 0.01 | A |  |  | R | L1 load current effective value | End User
1316 | 0524 | ActivePower_Load_L1N | I16 | 0.01 | kW |  |  | R | Load L1 to N active power | End User
1317 | 0525 | Voltage_Output_L2N | U16 | 0.1 | V |  |  | R | Effective value of inverter L2 to N voltage | End User
1318 | 0526 | Current_Load_L2N | I16 | 0.01 | A |  |  | R | L2 load current effective value | End User
1319 | 0527 | ActivePower_Load_L2N | I16 | 0.01 | kW |  |  | R | Load L2 to N active power | End User
1320 | 0528
1321 | 0529
1322 | 052A
1323 | 052B
1324 | 052C
1325 | 052D
1326 | 052E
1327 | 052F
1328 | 0530
1329 | 0531
1330 | 0532
1331 | 0533
1332 | 0534
1333 | 0535
1334 | 0536
1335 | 0537
1336 | 0538
1337 | 0539
1338 | 053A
1339 | 053B
1340 | 053C
1341 | 053D
1342 | 053E
1343 | 053F
PV input (0x0580-0x05FF)
1408 | 0580 | AddressMask_Realtime_Input_PV1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid | End User
1409 | 0581
1410 | 0582
1411 | 0583
1412 | 0584 | Voltage_PV1 | U16 | 0.1 | V |  |  | R | The first PV voltage | End User
1413 | 0585 | Current_PV1 | U16 | 0.01 | A |  |  | R | The first PV current | End User
1414 | 0586 | Power_PV1 | U16 | 0.01 | kW |  |  | R | PV power of the first road | End User
1415 | 0587 | Voltage_PV2 | U16 | 0.1 | V |  |  | R | The second PV voltage | End User
1416 | 0588 | Current_PV2 | U16 | 0.01 | A |  |  | R | The second PV current | End User
1417 | 0589 | Power_PV2 | U16 | 0.01 | kW |  |  | R | PV power of the 2nd road | End User
1418 | 058A | Voltage_PV3 | U16 | 0.1 | V |  |  | R | No. 3 PV voltage | End User
1419 | 058B | Current_PV3 | U16 | 0.01 | A |  |  | R | No. 3 PV current | End User
1420 | 058C | Power_PV3 | U16 | 0.01 | kW |  |  | R | No. 3 PV power | End User
1421 | 058D | Voltage_PV4 | U16 | 0.1 | V |  |  | R | No. 4 PV voltage | End User
1422 | 058E | Current_PV4 | U16 | 0.01 | A |  |  | R | No. 4 PV current | End User
1423 | 058F | Power_PV4 | U16 | 0.01 | kW |  |  | R | No. 4 PV power | End User
1424 | 0590 | Voltage_PV5 | U16 | 0.1 | V |  |  | R | No. 5 PV voltage | End User
1425 | 0591 | Current_PV5 | U16 | 0.01 | A |  |  | R | No. 5 PV current | End User
1426 | 0592 | Power_PV5 | U16 | 0.01 | kW |  |  | R | No. 5 PV power | End User
1427 | 0593 | Voltage_PV6 | U16 | 0.1 | V |  |  | R | No. 6 PV voltage | End User
1428 | 0594 | Current_PV6 | U16 | 0.01 | A |  |  | R | No. 6 PV current | End User
1429 | 0595 | Power_PV6 | U16 | 0.01 | kW |  |  | R | No. 6 PV power | End User
1430 | 0596 | Voltage_PV7 | U16 | 0.1 | V |  |  | R | No. 7 PV voltage | End User
1431 | 0597 | Current_PV7 | U16 | 0.01 | A |  |  | R | No. 7 PV current | End User
1432 | 0598 | Power_PV7 | U16 | 0.01 | kW |  |  | R | No. 7 PV power | End User
1433 | 0599 | Voltage_PV8 | U16 | 0.1 | V |  |  | R | No. 8 PV voltage | End User
1434 | 059A | Current_PV8 | U16 | 0.01 | A |  |  | R | No. 8 PV current | End User
1435 | 059B | Power_PV8 | U16 | 0.01 | kW |  |  | R | No. 8 PV power | End User
1436 | 059C | Voltage_PV9 | U16 | 0.1 | V |  |  | R | No. 9 PV voltage | End User
1437 | 059D | Current_PV9 | U16 | 0.01 | A |  |  | R | No. 9 PV current | End User
1438 | 059E | Power_PV9 | U16 | 0.01 | kW |  |  | R | No. 9 PV power | End User
1439 | 059F | Voltage_PV10 | U16 | 0.1 | V |  |  | R | No. 10 PV voltage | End User
1440 | 05A0 | Current_PV10 | U16 | 0.01 | A |  |  | R | No. 10 PV current | End User
1441 | 05A1 | Power_PV10 | U16 | 0.01 | kW |  |  | R | No. 10 PV power | End User
1442 | 05A2 | Voltage_PV11 | U16 | 0.1 | V |  |  | R | 11th PV voltage | End User
1443 | 05A3 | Current_PV11 | U16 | 0.01 | A |  |  | R | 11th PV current | End User
1444 | 05A4 | Power_PV11 | U16 | 0.01 | kW |  |  | R | 11th PV power | End User
1445 | 05A5 | Voltage_PV12 | U16 | 0.1 | V |  |  | R | 12th PV voltage | End User
1446 | 05A6 | Current_PV12 | U16 | 0.01 | A |  |  | R | 12th PV current | End User
1447 | 05A7 | Power_PV12 | U16 | 0.01 | kW |  |  | R | 12th PV power | End User
1448 | 05A8 | Voltage_PV13 | U16 | 0.1 | V |  |  | R | 13th PV voltage | End User
1449 | 05A9 | Current_PV13 | U16 | 0.01 | A |  |  | R | 13th PV current | End User
1450 | 05AA | Power_PV13 | U16 | 0.01 | kW |  |  | R | 13th PV power | End User
1451 | 05AB | Voltage_PV14 | U16 | 0.1 | V |  |  | R | No. 14 PV voltage | End User
1452 | 05AC | Current_PV14 | U16 | 0.01 | A |  |  | R | No. 14 PV current | End User
1453 | 05AD | Power_PV14 | U16 | 0.01 | kW |  |  | R | No. 14 PV power | End User
1454 | 05AE | Voltage_PV15 | U16 | 0.1 | V |  |  | R | 15th PV voltage | End User
1455 | 05AF | Current_PV15 | U16 | 0.01 | A |  |  | R | 15th PV current | End User
1456 | 05B0 | Power_PV15 | U16 | 0.01 | kW |  |  | R | 15th PV power | End User
1457 | 05B1 | Voltage_PV16 | U16 | 0.1 | V |  |  | R | 16th PV voltage | End User
1458 | 05B2 | Current_PV16 | U16 | 0.01 | A |  |  | R | 16th PV current | End User
1459 | 05B3 | Power_PV16 | U16 | 0.01 | kW |  |  | R | 16th PV power | End User
1460 | 05B4
1461 | 05B5
1462 | 05B6
1463 | 05B7
1464 | 05B8
1465 | 05B9
1466 | 05BA
1467 | 05BB
1468 | 05BC
1469 | 05BD
1470 | 05BE
1471 | 05BF
1472 | 05C0 | AddressMask_Realtime_Input_PV2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid. | End User
1473 | 05C1
1474 | 05C2
1475 | 05C3
1476 | 05C4 | Power_PV_Total | U16 | 0.1 | kW |  |  | R | Total PV power | End User
1477 | 05C5
1478 | 05C6
1479 | 05C7
1480 | 05C8
1481 | 05C9
1482 | 05CA
1483 | 05CB
1484 | 05CC
1485 | 05CD
1486 | 05CE
1487 | 05CF
1488 | 05D0
1489 | 05D1
1490 | 05D2
1491 | 05D3
1492 | 05D4
1493 | 05D5
1494 | 05D6
1495 | 05D7
1496 | 05D8
1497 | 05D9
1498 | 05DA
1499 | 05DB
1500 | 05DC
1501 | 05DD
1502 | 05DE
1503 | 05DF
1504 | 05E0
1505 | 05E1
1506 | 05E2
1507 | 05E3
1508 | 05E4
1509 | 05E5
1510 | 05E6
1511 | 05E7
1512 | 05E8
1513 | 05E9
1514 | 05EA
1515 | 05EB
1516 | 05EC
1517 | 05ED
1518 | 05EE
1519 | 05EF
1520 | 05F0
1521 | 05F1
1522 | 05F2
1523 | 05F3
Battery input (0x0600-0x067F)
1536 | 0600 | AddressMask_Realtime_Input_Bat1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid | End User
1537 | 0601
1538 | 0602
1539 | 0603
1540 | 0604 | Voltage_Bat1 | U16 | 0.1 | V |  |  | R | No. 1 battery pack voltage | End User
1541 | 0605 | Current_Bat1 | I16 | 0.01 | A |  |  | R | The charging and discharging current of the first battery pack. Charge is positive, discharge is negative | End User
1542 | 0606 | Power_Bat1 | I16 | 0.01 | kW |  |  | R | The charging and discharging power of the first battery pack. Charge is positive, discharge is negative | End User
1543 | 0607 | Temperature_Env_Bat1 | I16 | 1 | ℃ |  |  | R | Ambient temperature of the first battery pack | End User
1544 | 0608 | SOC_Bat1 | U16 | 1 | % |  |  | R | No. 1 battery pack SOC | End User
1545 | 0609 | SOH_Bat1 | U16 | 1 | % |  |  | R | No. 1 battery pack SOH | End User
1546 | 060A | ChargeCycle_Bat1 | U16 | 1 | cycle |  |  | R | Number of cycles of the first battery pack | End User
1547 | 060B | Voltage_Bat2 | U16 | 0.1 | V |  |  | R | No. 2 battery pack voltage | End User
1548 | 060C | Current_Bat2 | I16 | 0.01 | A |  |  | R | The charging and discharging current of the second battery pack. Charge is positive, discharge is negative | End User
1549 | 060D | Power_Bat2 | I16 | 0.01 | kW |  |  | R | The charging and discharging power of the second battery pack. Charge is positive, discharge is negative | End User
1550 | 060E | Temperature_Env_Bat2 | I16 | 1 | ℃ |  |  | R | Ambient temperature of the second battery pack | End User
1551 | 060F | SOC_Bat2 | U16 | 1 | % |  |  | R | 2nd battery pack SOC | End User
1552 | 0610 | SOH_Bat2 | U16 | 1 | % |  |  | R | 2nd battery pack SOH | End User
1553 | 0611 | ChargeCycle_Bat2 | U16 | 1 | cycle |  |  | R | Number of cycles of the second battery pack | End User
1554 | 0612 | Voltage_Bat3 | U16 | 0.1 | V |  |  | R | No. 3 battery pack voltage | End User
1555 | 0613 | Current_Bat3 | I16 | 0.01 | A |  |  | R | The charging and discharging current of the third battery pack. Charge is positive, discharge is negative | End User
1556 | 0614 | Power_Bat3 | I16 | 0.01 | kW |  |  | R | The charging and discharging power of the third battery pack. Charge is positive, discharge is negative | End User
1557 | 0615 | Temperature_Env_Bat3 | I16 | 1 | ℃ |  |  | R | Ambient temperature of the third battery pack | End User
1558 | 0616 | SOC_Bat3 | U16 | 1 | % |  |  | R | No. 3 battery pack SOC | End User
1559 | 0617 | SOH_Bat3 | U16 | 1 | % |  |  | R | No. 3 battery pack SOH | End User
1560 | 0618 | ChargeCycle_Bat3 | U16 | 1 | cycle |  |  | R | Number of cycles of the third battery pack | End User
1561 | 0619 | Voltage_Bat4 | U16 | 0.1 | V |  |  | R | No. 4 battery pack voltage | End User
1562 | 061A | Current_Bat4 | I16 | 0.01 | A |  |  | R | Charging and discharging current of No. 4 battery pack. Charge is positive, discharge is negative | End User
1563 | 061B | Power_Bat4 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of the 4th battery pack. Charge is positive, discharge is negative | End User
1564 | 061C | Temperature_Env_Bat4 | I16 | 1 | ℃ |  |  | R | Ambient temperature of battery pack No. 4 | End User
1565 | 061D | SOC_Bat4 | U16 | 1 | % |  |  | R | No. 4 battery pack SOC | End User
1566 | 061E | SOH_Bat4 | U16 | 1 | % |  |  | R | No. 4 battery pack SOH | End User
1567 | 061F | ChargeCycle_Bat4 | U16 | 1 | cycle |  |  | R | Number of cycles of the 4th battery pack | End User
1568 | 0620 | Voltage_Bat5 | U16 | 0.1 | V |  |  | R | No. 5 battery pack voltage | End User
1569 | 0621 | Current_Bat5 | I16 | 0.01 | A |  |  | R | No. 5 battery pack charging and discharging current. Charge is positive, discharge is negative | End User
1570 | 0622 | Power_Bat5 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of No. 5 battery pack. Charge is positive, discharge is negative | End User
1571 | 0623 | Temperature_Env_Bat5 | I16 | 1 | ℃ |  |  | R | Ambient temperature of battery pack No. 5 | End User
1572 | 0624 | SOC_Bat5 | U16 | 1 | % |  |  | R | No. 5 battery pack SOC | End User
1573 | 0625 | SOH_Bat5 | U16 | 1 | % |  |  | R | No. 5 battery pack SOH | End User
1574 | 0626 | ChargeCycle_Bat5 | U16 | 1 | cycle |  |  | R | Number of cycles of the 5th battery pack | End User
1575 | 0627 | Voltage_Bat6 | U16 | 0.1 | V |  |  | R | No. 6 battery pack voltage | End User
1576 | 0628 | Current_Bat6 | I16 | 0.01 | A |  |  | R | No. 6 battery pack charge and discharge current. Charge is positive, discharge is negative | End User
1577 | 0629 | Power_Bat6 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of No. 6 battery pack. Charge is positive, discharge is negative | End User
1578 | 062A | Temperature_Env_Bat6 | I16 | 1 | ℃ |  |  | R | Ambient temperature of the 6th battery pack | End User
1579 | 062B | SOC_Bat6 | U16 | 1 | % |  |  | R | 6th battery pack SOC | End User
1580 | 062C | SOH_Bat6 | U16 | 1 | % |  |  | R | No. 6 battery pack SOH | End User
1581 | 062D | ChargeCycle_Bat6 | U16 | 1 | cycle |  |  | R | Number of cycles of the 6th battery pack | End User
1582 | 062E | Voltage_Bat7 | U16 | 0.1 | V |  |  | R | No. 7 battery pack voltage | End User
1583 | 062F | Current_Bat7 | I16 | 0.01 | A |  |  | R | No. 7 battery pack charging and discharging current. Charge is positive, discharge is negative | End User
1584 | 0630 | Power_Bat7 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of No. 7 battery pack. Charge is positive, discharge is negative | End User
1585 | 0631 | Temperature_Env_Bat7 | I16 | 1 | ℃ |  |  | R | Ambient temperature of battery pack No. 7 | End User
1586 | 0632 | SOC_Bat7 | U16 | 1 | % |  |  | R | No. 7 battery pack SOC | End User
1587 | 0633 | SOH_Bat7 | U16 | 1 | % |  |  | R | No. 7 battery pack SOH | End User
1588 | 0634 | ChargeCycle_Bat7 | U16 | 1 | cycle |  |  | R | No. 7 battery pack cycle times | End User
1589 | 0635 | Voltage_Bat8 | U16 | 0.1 | V |  |  | R | No. 8 battery pack voltage | End User
1590 | 0636 | Current_Bat8 | I16 | 0.01 | A |  |  | R | Charging and discharging current of No. 8 battery pack. Charge is positive, discharge is negative | End User
1591 | 0637 | Power_Bat8 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of No. 8 battery pack. Charge is positive, discharge is negative | End User
1592 | 0638 | Temperature_Env_Bat8 | I16 | 1 | ℃ |  |  | R | Ambient temperature of the 8th battery pack | End User
1593 | 0639 | SOC_Bat8 | U16 | 1 | % |  |  | R | No. 8 battery pack SOC | End User
1594 | 063A | SOH_Bat8 | U16 | 1 | % |  |  | R | No. 8 battery pack SOH | End User
1595 | 063B | ChargeCycle_Bat8 | U16 | 1 | cycle |  |  | R | Number of cycles of the 8th battery pack | End User
1596 | 063C
1597 | 063D
1598 | 063E
1599 | 063F
1600 | 0640 | AddressMask_Realtime_Input_Bat2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid. | End User
1601 | 0641
1602 | 0642
1603 | 0643
1604 | 0644 | Voltage_Bat9 | U16 | 0.1 | V |  |  | R | No. 9 battery pack voltage | End User
1605 | 0645 | Current_Bat9 | I16 | 0.01 | A |  |  | R | No. 9 battery pack charging and discharging current. Charge is positive, discharge is negative | End User
1606 | 0646 | Power_Bat9 | I16 | 0.01 | kW |  |  | R | The charging and discharging power of the 9th battery pack. Charge is positive, discharge is negative | End User
1607 | 0647 | Temperature_Env_Bat9 | I16 | 1 | ℃ |  |  | R | Ambient temperature of the 9th battery pack | End User
1608 | 0648 | SOC_Bat9 | U16 | 1 | % |  |  | R | No. 9 battery pack SOC | End User
1609 | 0649 | SOH_Bat9 | U16 | 1 | % |  |  | R | No. 9 battery pack SOH | End User
1610 | 064A | ChargeCycle_Bat9 | U16 | 1 | cycle |  |  | R | Number of cycles of the 9th battery pack | End User
1611 | 064B | Voltage_Bat10 | U16 | 0.1 | V |  |  | R | No. 10 battery pack voltage | End User
1612 | 064C | Current_Bat10 | I16 | 0.01 | A |  |  | R | No. 10 battery pack charge and discharge current. Charge is positive, discharge is negative | End User
1613 | 064D | Power_Bat10 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of No. 10 battery pack. Charge is positive, discharge is negative | End User
1614 | 064E | Temperature_Env_Bat10 | I16 | 1 | ℃ |  |  | R | Ambient temperature of No. 10 battery pack | End User
1615 | 064F | SOC_Bat10 | U16 | 1 | % |  |  | R | No. 10 battery pack SOC | End User
1616 | 0650 | SOH_Bat10 | U16 | 1 | % |  |  | R | No. 10 battery pack SOH | End User
1617 | 0651 | ChargeCycle_Bat10 | U16 | 1 | cycle |  |  | R | Number of cycles of the 10th battery pack | End User
1618 | 0652 | Voltage_Bat11 | U16 | 0.1 | V |  |  | R | No. 11 battery pack voltage | End User
1619 | 0653 | Current_Bat11 | I16 | 0.01 | A |  |  | R | The charging and discharging current of No. 11 battery pack. Charge is positive, discharge is negative | End User
1620 | 0654 | Power_Bat11 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of No. 11 battery pack. Charge is positive, discharge is negative | End User
1621 | 0655 | Temperature_Env_Bat11 | I16 | 1 | ℃ |  |  | R | Ambient temperature of battery pack No. 11 | End User
1622 | 0656 | SOC_Bat11 | U16 | 1 | % |  |  | R | No. 11 battery pack SOC | End User
1623 | 0657 | SOH_Bat11 | U16 | 1 | % |  |  | R | No. 11 battery pack SOH | End User
1624 | 0658 | ChargeCycle_Bat11 | U16 | 1 | cycle |  |  | R | Number of cycles of the 11th battery pack | End User
1625 | 0659 | Voltage_Bat12 | U16 | 0.1 | V |  |  | R | No. 12 battery pack voltage | End User
1626 | 065A | Current_Bat12 | I16 | 0.01 | A |  |  | R | Charging and discharging current of No. 12 battery pack. Charge is positive, discharge is negative | End User
1627 | 065B | Power_Bat12 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of No. 12 battery pack. Charge is positive, discharge is negative | End User
1628 | 065C | Temperature_Env_Bat12 | I16 | 1 | ℃ |  |  | R | Ambient temperature of the 12th battery pack | End User
1629 | 065D | SOC_Bat12 | U16 | 1 | % |  |  | R | No. 12 battery pack SOC | End User
1630 | 065E | SOH_Bat12 | U16 | 1 | % |  |  | R | No. 12 battery pack SOH | End User
1631 | 065F | ChargeCycle_Bat12 | U16 | 1 | cycle |  |  | R | Number of cycles of the 12th battery pack | End User
1632 | 0660
1633 | 0661
1634 | 0662
1635 | 0663
1636 | 0664
1637 | 0665
1638 | 0666
1639 | 0667 | Power_Bat_Total | I16 | 0.1 | kW |  |  | R | Total battery charge and discharge power. Charge is positive, discharge is negative | End User
1640 | 0668 | SOC_Bat_Average | U16 | 1 | % |  |  | R | Summarize the average value of battery pack SOC | End User
1641 | 0669 | SOH_Bat | U16 | 1 | % |  |  | R | Summary battery pack SOH | End User
1642 | 066A
1643 | 066B
1644 | 066C
1645 | 066D
1646 | 066E
1647 | 066F
1648 | 0670
1649 | 0671
1650 | 0672
1651 | 0673
1652 | 0674
1653 | 0675
1654 | 0676
1655 | 0677
1656 | 0678
1657 | 0679
1658 | 067A
1659 | 067B
1660 | 067C
1661 | 067D
1662 | 067E
1663 | 067F
Power (0x0680-0x06BF)
1664 | 0680 | AddressMask_Realtime_ElectricityStatistics1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid. | End User
1665 | 0681
1666 | 0682
1667 | 0683
1668 | 0684 | PV_Generation_Today | U32 | 0.01 | kWh |  |  | R | Power generation of the day | End User
1669 | 0685
1670 | 0686 | PV_Generation_Total | U32 | 0.1 | kWh |  |  | R | Total power generation time | End User
1671 | 0687
1672 | 0688 | Load_Consumption_Today | U32 | 0.01 | kWh |  |  | R | Load power consumption of the day | End User
1673 | 0689
1674 | 068A | Load_Consumption_Total | U32 | 0.1 | kWh |  |  | R | Total load power consumption | End User
1675 | 068B
1676 | 068C | Energy_Purchase_Today | U32 | 0.01 | kWh |  |  | R | Buy electricity on the day | End User
1677 | 068D
1678 | 068E | Energy_Purchase_Total | U32 | 0.1 | kWh |  |  | R | Total electricity purchased | End User
1679 | 068F
1680 | 0690 | Energy_Selling_Today | U32 | 0.01 | kWh |  |  | R | Electricity sold on the day | End User
1681 | 0691
1682 | 0692 | Energy_Selling_Total | U32 | 0.1 | kWh |  |  | R | Total electricity sold | End User
1683 | 0693
1684 | 0694 | Bat_Charge_Today | U32 | 0.01 | kWh |  |  | R | Battery charge capacity of the day | End User
1685 | 0695
1686 | 0696 | Bat_Charge_Total | U32 | 0.1 | kWh |  |  | R | Total battery charge | End User
1687 | 0697
1688 | 0698 | Bat_Discharge_Today | U32 | 0.01 | kWh |  |  | R | Battery discharge capacity of the day | End User
1689 | 0699
1690 | 069A | Bat_Discharge_Total | U32 | 0.1 | kWh |  |  | R | Total battery discharge | End User
1691 | 069B
1692 | 069C
1693 | 069D
1694 | 069E
1695 | 069F
1696 | 06A0
1697 | 06A1
1698 | 06A2
1699 | 06A3
1700 | 06A4
1701 | 06A5
1702 | 06A6
1703 | 06A7
1704 | 06A8
1705 | 06A9
1706 | 06AA
1707 | 06AB
1708 | 06AC
1709 | 06AD
1710 | 06AE
1711 | 06AF
1712 | 06B0
1713 | 06B1
1714 | 06B2
1715 | 06B3
1716 | 06B4
1717 | 06B5
1718 | 06B6
1719 | 06B7
1720 | 06B8
1721 | 06B9
1722 | 06BA
1723 | 06BB
1724 | 06BC
1725 | 06BD
1726 | 06BE
1727 | 06BF
Internal info (0x06C0-0x06FF)
1728 | 06C0 | AddressMask_Realtime_ClassifiedInfo1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid | Installer
1729 | 06C1
1730 | 06C2
1731 | 06C3
1732 | 06C4 | GFCI | U16 | 1 | mA |  |  | R | Leakage current | Installer
1733 | 06C5 | Current_Bus_Balance | I16 | 0.01 | A |  |  | R | Balance current | Installer
1734 | 06C6 | DCI_R | I16 | 1 | mA |  |  | R | R-phase current DC component | Installer
1735 | 06C7 | DCI_S | I16 | 1 | mA |  |  | R | S-phase current DC component | Installer
1736 | 06C8 | DCI_T | I16 | 1 | mA |  |  | R | T-phase current DC component | Installer
1737 | 06C9 | DCV_R | I16 | 1 | mV |  |  | R | R-phase voltage DC component | Installer
1738 | 06CA | DCV_S | I16 | 1 | mV |  |  | R | S-phase voltage DC component | Installer
1739 | 06CB | DCV_T | I16 | 1 | mV |  |  | R | T-phase voltage DC component | Installer
1740 | 06CC | Voltage_Bus | U16 | 0.1 | V |  |  | R | Total BUS voltage | Installer
1741 | 06CD | Voltage_Bus_P | U16 | 0.1 | V |  |  | R | BUS positive voltage | Installer
1742 | 06CE | Voltage_Bus_N | U16 | 0.1 | V |  |  | R | BUS negative voltage | Installer
1743 | 06CF | Voltage_Bus_LLC | U16 | 0.1 | V |  |  | R | LLC Bus voltage | Installer
1744 | 06D0 | Current_BuckBoost | I16 | 0.01 | A |  |  | R | BuckBoost current | Installer
1745 | 06D1 | Voltage_Bus_P_Half | U16 | 0.1 | V |  |  | R | BUS positive half voltage
1746 | 06D2 | Voltage_Bus_N_Half | U16 | 0.1 | V |  |  | R | BUS negative half voltage
1747 | 06D3 | FlyingCap_Voltage1 | U16 | 0.1 | V |  |  | R | PV1 flying capacitor voltage
1748 | 06D4 | FlyingCap_Voltage2 | U16 | 0.1 | V |  |  | R | PV2 flying capacitor voltage
1749 | 06D5 | FlyingCap_Voltage3 | U16 | 0.1 | V |  |  | R | PV3 flying capacitor voltage
1750 | 06D6 | FlyingCap_Voltage4 | U16 | 0.1 | V |  |  | R | PV4 flying capacitor voltage
1751 | 06D7 | FlyingCap_Voltage5 | U16 | 0.1 | V |  |  | R | PV5 flying capacitor voltage
1752 | 06D8 | FlyingCap_Voltage6 | U16 | 0.1 | V |  |  | R | PV6 flying capacitor voltage
1753 | 06D9 | FlyingCap_Voltage7 | U16 | 0.1 | V |  |  | R | PV7 flying capacitor voltage
1754 | 06DA | FlyingCap_Voltage8 | U16 | 0.1 | V |  |  | R | PV8 flying capacitor voltage
1755 | 06DB | FlyingCap_Voltage9 | U16 | 0.1 | V |  |  | R | PV9 flying capacitor voltage
1756 | 06DC | FlyingCap_Voltage10 | U16 | 0.1 | V |  |  | R | PV10 flying capacitor voltage
1757 | 06DD | FlyingCap_Voltage11 | U16 | 0.1 | V |  |  | R | PV11 flying capacitor voltage
1758 | 06DE | FlyingCap_Voltage12 | U16 | 0.1 | V |  |  | R | PV12 flying capacitor voltage
1759 | 06DF | FlyingCap_Voltage13 | U16 | 0.1 | V |  |  | R | PV13 flying capacitor voltage
1760 | 06E0 | FlyingCap_Voltage14 | U16 | 0.1 | V |  |  | R | PV14 flying capacitor voltage
1761 | 06E1 | FlyingCap_Voltage15 | U16 | 0.1 | V |  |  | R | PV15 flying capacitor voltage
1762 | 06E2 | FlyingCap_Voltage16 | U16 | 0.1 | V |  |  | R | PV16 flying capacitor voltage
1763 | 06E3
1764 | 06E4
1765 | 06E5
1766 | 06E6
1767 | 06E7
1768 | 06E8
1769 | 06E9
1770 | 06EA
1771 | 06EB
1772 | 06EC
1773 | 06ED
1774 | 06EE
1775 | 06EF
1776 | 06F0
1777 | 06F1
1778 | 06F2
1779 | 06F3
1780 | 06F4
1781 | 06F5
1782 | 06F6
1783 | 06F7
1784 | 06F8
1785 | 06F9
1786 | 06FA
1787 | 06FB
1788 | 06FC
1789 | 06FD
1790 | 06FE
1791 | 06FF
Combined info (0x0700-0x077F)
1792 | 0700 | AddressMask_Realtime_CombinerInfo1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid | Installer
1793 | 0701
1794 | 0702
1795 | 0703
1796 | 0704 | Voltage_Group1 | U16 | 0.1 | V |  |  | R | The first group of bus voltage
1797 | 0705 | Current_Group1_Branch1 | U16 | 0.01 | A |  |  | R | The first group of the first string current
1798 | 0706 | Current_Group1_Branch2 | U16 | 0.01 | A |  |  | R | The first group and the second string current
1799 | 0707 | Voltage_Group2 | U16 | 0.1 | V |  |  | R | The second group of bus voltage
1800 | 0708 | Current_Group2_Branch1 | U16 | 0.01 | A |  |  | R | 2nd group 1st string current
1801 | 0709 | Current_Group2_Branch2 | U16 | 0.01 | A |  |  | R | 2nd group 2nd string current
1802 | 070A | Voltage_Group3 | U16 | 0.1 | V |  |  | R | The third group of bus voltage
1803 | 070B | Current_Group3_Branch1 | U16 | 0.01 | A |  |  | R | 3rd group 1st string current
1804 | 070C | Current_Group3_Branch2 | U16 | 0.01 | A |  |  | R | 3rd group 2nd string current
1805 | 070D | Voltage_Group4 | U16 | 0.1 | V |  |  | R | Group 4 bus voltage
1806 | 070E | Current_Group4_Branch1 | U16 | 0.01 | A |  |  | R | 4th group 1st string current
1807 | 070F | Current_Group4_Branch2 | U16 | 0.01 | A |  |  | R | 4th group 2nd string current
1808 | 0710 | Voltage_Group5 | U16 | 0.1 | V |  |  | R | Group 5 bus voltage
1809 | 0711 | Current_Group5_Branch1 | U16 | 0.01 | A |  |  | R | 5th group 1st string current
1810 | 0712 | Current_Group5_Branch2 | U16 | 0.01 | A |  |  | R | 5th group 2nd string current
1811 | 0713 | Voltage_Group6 | U16 | 0.1 | V |  |  | R | Group 6 bus voltage
1812 | 0714 | Current_Group6_Branch1 | U16 | 0.01 | A |  |  | R | 6th group 1st string current
1813 | 0715 | Current_Group6_Branch2 | U16 | 0.01 | A |  |  | R | 6th group 2nd string current
1814 | 0716 | Voltage_Group7 | U16 | 0.1 | V |  |  | R | Group 7 bus voltage
1815 | 0717 | Current_Group7_Branch1 | U16 | 0.01 | A |  |  | R | 7th group 1st string current
1816 | 0718 | Current_Group7_Branch2 | U16 | 0.01 | A |  |  | R | 7th group 2nd string current
1817 | 0719 | Voltage_Group8 | U16 | 0.1 | V |  |  | R | Group 8 bus voltage
1818 | 071A | Current_Group8_Branch1 | U16 | 0.01 | A |  |  | R | 8th group 1st string current
1819 | 071B | Current_Group8_Branch2 | U16 | 0.01 | A |  |  | R | 8th group 2nd string current
1820 | 071C | Voltage_Group9 | U16 | 0.1 | V |  |  | R | Group 9 bus voltage
1821 | 071D | Current_Group9_Branch1 | U16 | 0.01 | A |  |  | R | 9th group 1st string current
1822 | 071E | Current_Group9_Branch2 | U16 | 0.01 | A |  |  | R | 9th group 2nd string current
1823 | 071F | Voltage_Group10 | U16 | 0.1 | V |  |  | R | Group 10 bus voltage
1824 | 0720 | Current_Group10_Branch1 | U16 | 0.01 | A |  |  | R | 10th group 1st string current
1825 | 0721 | Current_Group10_Branch2 | U16 | 0.01 | A |  |  | R | 10th group 2nd string current
1826 | 0722 | Voltage_Group11 | U16 | 0.1 | V |  |  | R | Group 11 bus voltage
1827 | 0723 | Current_Group11_Branch1 | U16 | 0.01 | A |  |  | R | 11th group 1st string current
1828 | 0724 | Current_Group11_Branch2 | U16 | 0.01 | A |  |  | R | 11th group 2nd string current
1829 | 0725 | Voltage_Group12 | U16 | 0.1 | V |  |  | R | The 12th group of bus voltage
1830 | 0726 | Current_Group12_Branch1 | U16 | 0.01 | A |  |  | R | 12th group 1st string current
1831 | 0727 | Current_Group12_Branch2 | U16 | 0.01 | A |  |  | R | 12th group 2nd string current
1832 | 0728 | Voltage_Group13 | U16 | 0.1 | V |  |  | R | Group 13 bus voltage
1833 | 0729 | Current_Group13_Branch1 | U16 | 0.01 | A |  |  | R | 13th group 1st string current
1834 | 072A | Current_Group13_Branch2 | U16 | 0.01 | A |  |  | R | 13th group 2nd string current
1835 | 072B | Voltage_Group14 | U16 | 0.1 | V |  |  | R | Group 14 bus voltage
1836 | 072C | Current_Group14_Branch1 | U16 | 0.01 | A |  |  | R | The 14th group and the 1st string current
1837 | 072D | Current_Group14_Branch2 | U16 | 0.01 | A |  |  | R | The 14th group and the 2nd string current
1838 | 072E | Voltage_Group15 | U16 | 0.1 | V |  |  | R | Group 15 bus voltage
1839 | 072F | Current_Group15_Branch1 | U16 | 0.01 | A |  |  | R | 15th group 1st string current
1840 | 0730 | Current_Group15_Branch2 | U16 | 0.01 | A |  |  | R | 15th group 2nd string current
1841 | 0731 | Voltage_Group16 | U16 | 0.1 | V |  |  | R | The 16th group of bus voltage
1842 | 0732 | Current_Group16_Branch1 | U16 | 0.01 | A |  |  | R | The 16th group of the first string current
1843 | 0733 | Current_Group16_Branch2 | U16 | 0.01 | A |  |  | R | 16th group 2nd string current
1844 | 0734
1845 | 0735
1846 | 0736
1847 | 0737
1848 | 0738
1849 | 0739
1850 | 073A
1851 | 073B
1852 | 073C
1853 | 073D
1854 | 073E
1855 | 073F
1856 | 0740 | AddressMask_Realtime_CombinerInfo2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid | Installer
1857 | 0741
1858 | 0742
1859 | 0743
1860 | 0744
1861 | 0745
1862 | 0746
1863 | 0747
1864 | 0748
1865 | 0749
1866 | 074A
1867 | 074B
1868 | 074C
1869 | 074D
1870 | 074E
1871 | 074F
1872 | 0750
1873 | 0751
1874 | 0752
1875 | 0753
1876 | 0754
1877 | 0755
1878 | 0756
1879 | 0757
1880 | 0758
1881 | 0759
1882 | 075A
1883 | 075B
1884 | 075C
1885 | 075D
1886 | 075E
1887 | 075F
1888 | 0760
1889 | 0761
1890 | 0762
1891 | 0763
1892 | 0764
1893 | 0765
1894 | 0766
1895 | 0767
1896 | 0768
1897 | 0769
1898 | 076A
1899 | 076B
1900 | 076C
1901 | 076D
1902 | 076E
1903 | 076F
1904 | 0770
1905 | 0771
1906 | 0772
1907 | 0773
1908 | 0774
1909 | 0775
1910 | 0776
1911 | 0777
1912 | 0778
1913 | 0779
1914 | 077A
1915 | 077B
1916 | 077C
1917 | 077D
1918 | 077E
1919 | 077F
Arcing information (0x0780-0x07BF)
1920 | 0780 | AddressMask_Realtime_ArcInfo3 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid | Installer
1921 | 0781
1922 | 0782
1923 | 0783
1924 | 0784 | ArcStrength_Channel1 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 1
1925 | 0785 | ArcStrength_Channel2 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 2
1926 | 0786 | ArcStrength_Channel3 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 3
1927 | 0787 | ArcStrength_Channel4 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 4
1928 | 0788 | ArcStrength_Channel5 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 5
1929 | 0789 | ArcStrength_Channel6 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 6
1930 | 078A | ArcStrength_Channel7 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 7
1931 | 078B | ArcStrength_Channel8 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 8
1932 | 078C | ArcStrength_Channel9 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 9
1933 | 078D | ArcStrength_Channel10 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 10
1934 | 078E | ArcStrength_Channel11 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 11
1935 | 078F | ArcStrength_Channel12 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 12
1936 | 0790 | ArcStrength_Channel13 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 13
1937 | 0791 | ArcStrength_Channel14 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 14
1938 | 0792 | ArcStrength_Channel15 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 15
1939 | 0793 | ArcStrength_Channel16 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 16
1940 | 0794 | ArcStrength_Channel17 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 17
1941 | 0795 | ArcStrength_Channel18 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 18
1942 | 0796 | ArcStrength_Channel19 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 19
1943 | 0797 | ArcStrength_Channel20 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 20
1944 | 0798 | ArcStrength_Channel21 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 21
1945 | 0799 | ArcStrength_Channel22 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 22
1946 | 079A | ArcStrength_Channel23 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 23
1947 | 079B | ArcStrength_Channel24 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 24
1948 | 079C | ArcStrength_Channel25 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 25
1949 | 079D | ArcStrength_Channel26 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 26
1950 | 079E | ArcStrength_Channel27 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 27
1951 | 079F | ArcStrength_Channel28 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 28
1952 | 07A0 | ArcStrength_Channel29 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 29
1953 | 07A1 | ArcStrength_Channel30 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 30
1954 | 07A2 | ArcStrength_history_Channel1 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 1 is powered on Maximum value, automatically cleared after power failure
1955 | 07A3 | ArcStrength_history_Channel2 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 2 is powered on Maximum value, automatically cleared after power failure
1956 | 07A4 | ArcStrength_history_Channel3 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 3 is powered on Maximum value, automatically cleared after power failure
1957 | 07A5 | ArcStrength_history_Channel4 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 4 is powered on Maximum value, automatically cleared after power failure
1958 | 07A6 | ArcStrength_history_Channel5 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 5 is powered on Maximum value, automatically cleared after power failure
1959 | 07A7 | ArcStrength_history_Channel6 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 6 is powered on Maximum value, automatically cleared after power failure
1960 | 07A8 | ArcStrength_history_Channel7 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 7 is powered on Maximum value, automatically cleared after power failure
1961 | 07A9 | ArcStrength_history_Channel8 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 8 is powered on Maximum value, automatically cleared after power failure
1962 | 07AA | ArcStrength_history_Channel9 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 9 is powered on Maximum value, automatically cleared after power failure
1963 | 07AB | ArcStrength_history_Channel10 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 10 is powered on Maximum value, automatically cleared after power failure
1964 | 07AC | ArcStrength_history_Channel11 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 11 is powered on Maximum value, automatically cleared after power failure
1965 | 07AD | ArcStrength_history_Channel12 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 12 is powered on Maximum value, automatically cleared after power failure
1966 | 07AE | ArcStrength_history_Channel13 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 13 is powered on Maximum value, automatically cleared after power failure
1967 | 07AF | ArcStrength_history_Channel14 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 14 is powered on Maximum value, automatically cleared after power failure
1968 | 07B0 | ArcStrength_history_Channel15 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 15 is powered on Maximum value, automatically cleared after power failure
1969 | 07B1 | ArcStrength_history_Channel16 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 16 is powered on Maximum value, automatically cleared after power failure
1970 | 07B2 | ArcStrength_history_Channel17 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 17 is powered on Maximum value, automatically cleared after power failure
1971 | 07B3 | ArcStrength_history_Channel18 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 18 is powered on Maximum value, automatically cleared after power failure
1972 | 07B4 | ArcStrength_history_Channel19 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 19 is powered on Maximum value, automatically cleared after power failure
1973 | 07B5 | ArcStrength_history_Channel20 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 20 is powered on Maximum value, automatically cleared after power failure
1974 | 07B6 | ArcStrength_history_Channel21 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 21 is powered on Maximum value, automatically cleared after power failure
1975 | 07B7 | ArcStrength_history_Channel22 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 22 is powered on Maximum value, automatically cleared after power failure
1976 | 07B8 | ArcStrength_history_Channel23 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 23 is powered on Maximum value, automatically cleared after power failure
1977 | 07B9 | ArcStrength_history_Channel24 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 24 is powered on Maximum value, automatically cleared after power failure
1978 | 07BA | ArcStrength_history_Channel25 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 25 is powered on Maximum value, automatically cleared after power failure
1979 | 07BB | ArcStrength_history_Channel26 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 26 is powered on Maximum value, automatically cleared after power failure
1980 | 07BC | ArcStrength_history_Channel27 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 27 is powered on Maximum value, automatically cleared after power failure
1981 | 07BD | ArcStrength_history_Channel28 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 28 is powered on Maximum value, automatically cleared after power failure
1982 | 07BE | ArcStrength_history_Channel29 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 29 is powered on Maximum value, automatically cleared after power failure
1983 | 07BF | ArcStrength_history_Channel30 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 30 is powered on Maximum value, automatically cleared after power failure
Safety Parameter Area(0x0800-0x0FFF)
Boot Parameters (0x0800-0x083F)
2048 | 0800 | ConnectWaitTime | U16 | 1 | Second | 1 | 65535 | RW | Waiting time before generate on grid power | Installer
2049 | 0801 | PowerUpSpeed | U16 | 1 | %Pn/min | 1 | 3000 | RW | 100 mean fully power sided in one minute, Other values are calculated based on this | Installer
2050 | 0802 | ReconnectWaitTime | U16 | 1 | Second | 1 | 65535 | RW | Waiting time after grid fault recovery | Installer
2051 | 0803 | ReconnectPowerUpSpeed | U16 | 1 | %Pn/min | 1 | 3000 | RW | 100 mean fully power sided in one minute, Other values are calculated based on this | Installer
2052 | 0804 | VoltHighLimit | U16 | 0.1 | V | 0 | 65535 | RW | Upper limit for starting voltage (Grid side) | End User
2053 | 0805 | VoltLowLimit | U16 | 0.1 | V | 0 | 65535 | RW | Lower limit for starting Voltage (Grid Side) | End User
2054 | 0806 | FreqHighLimit | U16 | 0.01 | Hz | 4000 | 7000 | RW | Upper limit for starting frequency (Grid side) | End User
2055 | 0807 | FreqLowLimit | U16 | 0.01 | Hz | 4000 | 7000 | RW | Lower limit for starting Frequency (Grid Side) | End User
2056 | 0808 | ReconnectVoltHighLimit | U16 | 0.1 | V | 0 | 65535 | RW | Upper limit for reconnected grid voltage | End User
2057 | 0809 | ReconnectVoltLowLimit | U16 | 0.1 | V | 0 | 65535 | RW | Lower limit For reconnected grid voltage | End User
2058 | 080A | ReconnectFreqHighLimit | U16 | 0.01 | Hz | 4000 | 7000 | RW | Upper limit for reconnected grid frequency | End User
2059 | 080B | ReconnectFreqLowLimit | U16 | 0.01 | Hz | 4000 | 7000 | RW | Lower limit for reconnected grid frequency | End User
Grid voltage protection Parameters (0x0840-0x087F)
2112 | 0840 | Voltage Config | U16 |  |  |  |  | RW | Bit0：OV1 protection enable bits Bit1：OV2 protection enable bits Bit2：OV3 protection enable bit Bit3：UV1 protection enable bits Bit4：UV2 protection enable bits Bit5：UV3 Protection enable bits Bit6：over voltage protection enable bits(ten minutes time period) | Installer
2113 | 0841 | RatedVoltage | U16 | 0.1 | V | 0 | 65535 | RW | Grid Rated voltage | Installer
2114 | 0842 | FirstOvervoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | OV1 trigger Value | End User
2115 | 0843 | FirstOvervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | OV1 trigger time | Installer
2116 | 0844 | SecondOvervoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | OV2 Trigger Value | End User
2117 | 0845 | SecondOvervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | OV2 Trigger time | Installer
2118 | 0846 | ThirdOvervoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | OV3 Trigger value | End User
2119 | 0847 | ThirdOvervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | OV3 Trigger Time | Installer
2120 | 0848 | FirstUnderVoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | UV1 trigger Value | End User
2121 | 0849 | FirstUndervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | UV1 trigger time | Installer
2122 | 084A | SecondUnderVoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | UV2 Trigger Value | End User
2123 | 084B | SecondUndervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | UV2 Trigger time | Installer
2124 | 084C | ThirdUnderVoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | UV3 Trigger value | End User
2125 | 084D | ThirdUndervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | UV3 Trig+K852:K863ger Time | Installer
2126 | 084E | 10MinOvervoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | Over Voltage protection for Ten minutes range | Installer
Frquency Protection Parameter (0x0880-0x08BF)
2176 | 0880 | FrequencyConfig | U16 |  |  |  |  | RW | Bit0：OF1 protection enable bits Bit1：OF2 protection enable bits Bit2：OF3 protection enable bit Bit3：UF1 protection enable bits Bit4：UF2 protection enable bits Bit5：UF3 Protection enable bits | Installer
2177 | 0881 | RatedFrequency | U16 | 0.01 | Hz | 4000 | 7000 | RW | Grid Rated Frequency | Installer
2178 | 0882 | FirstOverfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | OF1 Trigger Value | End User
2179 | 0883 | FirstOverfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | OF1 trigger time | Installer
2180 | 0884 | SecondOverfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | OF2 Trigger Value | End User
2181 | 0885 | SecondOverfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | OF2 Trigger time | Installer
2182 | 0886 | ThirdOverfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | OF3 Trigger value | End User
2183 | 0887 | ThirdOverfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | OF3 Trigger Time | Installer
2184 | 0888 | FirstUnderfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | UF1 trigger Value | End User
2185 | 0889 | FirstUnderfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | UF1 trigger time | Installer
2186 | 088A | SecondUnderfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | UF2 Trigger Value | End User
2187 | 088B | SecondUnderfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | UF2 Trigger time | Installer
2188 | 088C | ThirdUnderfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | UF3 Trigger value | End User
2189 | 088D | ThirdUnderfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | UF3 Trigger Time | Installer
DCIProtection Parameter (0x08C0-0x08FF)
2240 | 08C0 | DCI Config | U16 |  |  |  |  | RW | Bit0：DCI level 1 protection Bit1：DCI level 2 protection Bit2：DCI level 3 protection Bit3：DCI testing enable bot | Installer
2241 | 08C1 | DCIFirstProtectionValue | U16 | 1 | mA | 1 | 65535 | RW | DCI level 1 tripping value | Installer
2242 | 08C2 | DCIFirstProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | DCI level 1 tripping time | Installer
2243 | 08C3 | DCISecondProtectionValue | U16 | 1 | mA | 1 | 65535 | RW | DCI level 2 tripping value | Installer
2244 | 08C4 | DCISecondProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | DCI level 2 tripping tie | Installer
2245 | 08C5 | DCIThirdProtectionValue | U16 | 1 | mA | 1 | 65535 | RW | DCI level 3 tripping value | Installer
2246 | 08C6 | DCIThirdProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | DCI level 3 tripping time | Installer
2247 | 08C7 | DCITestValue1 | I16 | 1 | mA | -32768 | 32767 | RW | DCI phase R testing value | Installer
2248 | 08C8 | DCITestValue2 | I16 | 1 | mA | -32768 | 32767 | RW | DCI phase S testing value | Installer
2249 | 08C9 | DCITestValue3 | I16 | 1 | mA | -32768 | 32767 | RW | DCI phase T testing value | Installer
2250 | 08CA | DCIFirstProtectionProportion | U16 | 0.01 | % | 1 | 65535 | RW | DCI level 1 protection Ratio | Installer
2251 | 08CB | DCISecondProtectionProportion | U16 | 0.01 | % | 1 | 65535 | RW | DCI level 2 protection Ratio | Installer
2252 | 08CC | DCIThirdProtectionProportion | U16 | 0.01 | % | 1 | 65535 | RW | DCI level 3 protection Ratio | Installer
Active power &Over/Under voltage Power Derate Paramter (0x0900-0x093F)
2304 | 0900 | Remote Config | U16 |  |  |  |  | RW | Bit0：Active power derate Bit1：remtely on/off control Bit2：power derate leading by high AC voltage Bit3：battery charging power derate leading high voltage Bit4：battery charging power derate by low voltage Bit5：DRM0 Bit6：logic interface（DRM1-8） Bit7：reflux power overload（VDE4105） | Installer
2305 | 0901 | ActiveOutputLimit | U16 | 0.1 | % | 0 | 1000 | RW | The percentage of active power output | Installer
2306 | 0902 | ActiveOutputDownSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | active power derating rate | Installer
2307 | 0903 | GridVoltageDropStart | U16 | 0.1 | V | 0 | 65535 | RW | the start point of power derate leading by high grid voltage | Installer
2308 | 0904 | GridVoltageDropStop | U16 | 0.1 | V | 0 | 65535 | RW | the end point of power derate leading by high ac voltage | Installer
2309 | 0905 | GridVoltageDropMinPower | I16 | 1 | % | -100 | 100 | RW | cut -off power of power derate leading by high ac voltage | Installer
2310 | 0906 | OvervoltageDownSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | power derating rate leading by high ac voltage | Installer
2311 | 0907 | ChgDerateVoltStart | U16 | 0.1 | V | 0 | 65535 | RW | the start point of power derate leading by low grid voltage | Installer
2312 | 0908 | ChgDerateVoltEnd | U16 | 0.1 | V | 0 | 65535 | RW | the end point of power derate leading by low ac voltage | Installer
2313 | 0909 | ChgDerateMinPower | I16 | 1 | % | -100 | 100 | RW | cut -off power of power derate leading by low ac voltage | Installer
2314 | 090A | PowerForLogic1 | I16 | 1 | % | -100 | 100 | RW | logic interface 1 corresponding power | Installer
2315 | 090B | PowerForLogic2 | I16 | 1 | % | -100 | 100 | RW | logic interface 2 corresponding power | Installer
2316 | 090C | PowerForLogic3 | I16 | 1 | % | -100 | 100 | RW | logic interface 3 corresponding power | Installer
2317 | 090D | PowerForLogic4 | I16 | 1 | % | -100 | 100 | RW | logic interface 4 corresponding power | Installer
2318 | 090E | PowerForLogic5 | I16 | 1 | % | -100 | 100 | RW | logic interface 5 corresponding power | Installer
2319 | 090F | PowerForLogic6 | I16 | 1 | % | -100 | 100 | RW | logic interface 6 corresponding power | Installer
2320 | 0910 | PowerForLogic7 | I16 | 1 | % | -100 | 100 | RW | logic interface 7 corresponding power | Installer
2321 | 0911 | PowerForLogic8 | I16 | 1 | % | -100 | 100 | RW | logic interface 8 corresponding power | Installer
2322 | 0912 | RefluxPower | U16 | 1 | % | 0 | 100 | RW | Reflux power (upper limit of VDE4105 safety grid-connected power) | Installer
2323 | 0913 | RefluxOVloadTime | U16 | 10 | ms | 0 | 65535 | RW | Reflux power over load (upper limit of VDE4105 safety grid-connected power) | Installer
2324 | 0914 | LogicDerateSpeed | U16 | 1 | %Pn/min | 1 | 65535 | RW | Logical interface derating rate | Installer
2325 | 0915 | LogicReloadSpeed | U16 | 1 | %Pn/min | 1 | 65535 | RW | Logical interface reload rate | Installer
2326 | 0916 | VoltageDerateResponseTime | U16 | 1 | Second | 0 | 65535 | RW | Voltage derate time | Installer
Over/Under Frquency Power Derate (0x0940-0x097F)
2368 | 0940 | FrequencyDerateConfig | U16 |  |  |  |  | RW | Bit0：enable, higher frequency power derate Bit1：enable, lower frequency power derate Bit2：enable, higher frequency power reload Bit3：enable, lower frequency power reload Bit4：enable,power derate start from rated power Bit5：enable,derating slope calculate by current power Bit12-13：derating mode(0: slope mode ; 1:frquency mode) | Installer
2369 | 0941 | OverfrequencyStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | the Starting point of power derate leading by higher frequency | Installer
2370 | 0942 | OverfrequencyEnd | U16 | 0.01 | Hz | 4000 | 7000 | RW | The ending point of power derate leading by higher frequency | Installer
2371 | 0943 | OverfrequencySlope | U16 | 1 | %Pn/Hz | 1 | 300 | RW | the percentage of power derate leading higher frequency German Standard slope=1/(s*fn) | Installer
2372 | 0944 | OverfrequencyResponseDelay | U16 | 10 | ms | 0 | 65535 | RW | waiting time for power derate leading by higher frequency | Installer
2373 | 0945 | OverfrequencyReloadDelay | U16 | 10 | ms | 0 | 65535 | RW | waiting time for power reload leading by higher frequency | Installer
2374 | 0946 | OverfrequencyReloadStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | reload frequency for power reload leading by higher frequency | Installer
2375 | 0947 | OverfrequencyReloadSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | the percentage of power reload rate leading by higher frequency | Installer
2376 | 0948 | UnderfrequencyStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | the Starting point of power derate leading by lower frequency | Installer
2377 | 0949 | UnderfrequencyEnd | U16 | 0.01 | Hz | 4000 | 7000 | RW | The ending point of power derate leading by lower frequency | Installer
2378 | 094A | UnderfrequencySlope | U16 | 1 | %Pn/Hz | 1 | 300 | RW | the percentage of power derate leading lower frequency German Standard slope=1/(s*fn) | Installer
2379 | 094B | UnderfrequencyResponseDelay | U16 | 10 | ms | 0 | 65535 | RW | waiting time for power derate leading by lower frequency | Installer
2380 | 094C | UnderfrequencyReloadDelay | U16 | 10 | ms | 0 | 65535 | RW | waiting time for power reload leading by lower frequency | Installer
2381 | 094D | UnderfrequencyReloadStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | reload frequency for power reload leading by lower frequency | Installer
2382 | 094E | UnderfrequencyReloadSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | the percentage of power reload rate leading by lower frequency | Installer
2383 | 094F | FrequencyRecoverMax | U16 | 0.01 | Hz | 4000 | 7000 | RW | Highest frequency to exist load reduction. | Installer
2384 | 0950 | FrequencyRecoverMin | U16 | 0.01 | Hz | 4000 | 7000 | RW | lowest frequency to exist load reduction. | Installer
2385 | 0951 | ESSOverFrequencyStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Over-frequency derate start frequency | Installer
2386 | 0952 | ESSOverfrequencyEnd | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) cut-off frequency for over-frequency derate. Frequency range mode is valid | Installer
2387 | 0953 | ESSOverFrequencySlope | U16 | 1 | %Pn/Hz | 1 | 300 | RW | (Energy storage) Over-frequency derate slope percentage. Slope mode is valid German standard slope=1/(s*fn) | Installer
2388 | 0954 | ESSOverFrequencyResponseDelay | U16 | 10 | ms | 0 | 65535 | RW | (Energy storage) Over-frequency derate start-up waiting time | Installer
2389 | 0955 | ESSOverFrequencyReloadDelay | U16 | 10 | ms | 0 | 65535 | RW | (Energy storage) Waiting time before over-frequency reload | Installer
2390 | 0956 | ESSOverfrequencyReloadStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Over-frequency derate reloading frequency. It takes effect when over-frequency reload is prohibited. | Installer
2391 | 0957 | ESSOverFrequencyReloadSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | (Energy storage) Over-frequency reload rate percentage | Installer
2392 | 0958 | ESSUnderFrequencyStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Under-frequency derate start frequency | Installer
2393 | 0959 | ESSUnderfrequencyEnd | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) cut-off frequency of under-frequency derate. Frequency range mode is valid | Installer
2394 | 095A | ESSUnderFrequencySlope | U16 | 1 | %Pn/Hz | 1 | 300 | RW | (Energy storage) Under-frequency derate slope percentage. Slope mode is valid | Installer
2395 | 095B | ESSUnderFrequencyResponseDelay | U16 | 10 | ms | 0 | 65535 | RW | (Energy storage) Under-frequency derate start-up waiting time | Installer
2396 | 095C | ESSUnderFrequencyReloadDelay | U16 | 10 | ms | 0 | 65535 | RW | (Energy storage) waiting time before under-frequency reload | Installer
2397 | 095D | ESSUnderfrequencyReloadStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Under-frequency derate reloading frequency. It takes effect when Under-frequency reload is prohibited. | Installer
2398 | 095E | ESSUnderFrequencyReloadSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | (Energy storage) Percentage of under-frequency reload rate | Installer
2399 | 095F | ESSFrequencyRecoverMax | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) The highest frequency for exiting derate. Over&Under-frequency sharing | Installer
2400 | 0960 | ESSFrequencyRecoverMin | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) The lowest frequency for exiting derate. Over&Under-frequency sharing | Installer
2401 | 0961 | ESSOverFrequencyTransition | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Over-frequency derate power crosses the frequency point. It is valid when 0940 Bit6 is enabled. | Installer
2402 | 0962 | ESSUnderFrequencyTransition | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Under-frequency derate power crosses the frequency point. It is valid when 0940 Bit6 is enabled. | Installer
Reactive power Parameter (0x0980-0x09BF)
2432 | 0980 | ReactiveConfig | U16 |  |  |  |  | RW | Bit0：enable reactive power Bit1-3：reactive power mode Bit8：enable, reactive mode 3 (voltage mode ) | Installer
2433 | 0981 | PowerFactor | I16 | 0.0001 |  | -10000 | 10000 | RW | power factor, by using reactive mode 1 to calculate Tanphi | Installer
2434 | 0982 | FixedReactivePercentage | I16 | 0.01 | % | -6000 | 6000 | RW | fixed percentage pf reactive power, calculate the reactive power by using reactive mode 2 | Installer
2435 | 0983 | ReactiveCos1 | I16 | 0.0001 |  | -10000 | 10000 | RW | For reactive mode 3，the 1st point power factor | Installer
2436 | 0984 | ReactivedynamicValue1 | I16 | 1 | % | -100 | 100 | RW | For reactive mode 3, the 1st point power percentage | Installer
2437 | 0985 | ReactiveCos2 | I16 | 0.0001 |  | -10000 | 10000 | RW | For reactive mode 3，the 2nd point power factor | Installer
2438 | 0986 | ReactivedynamicValue2 | I16 | 1 | % | -100 | 100 | RW | For reactive mode 3, the 2nd point power percentage | Installer
2439 | 0987 | ReactiveCos3 | I16 | 0.0001 |  | -10000 | 10000 | RW | For reactive mode 3，the 3rd point power factor | Installer
2440 | 0988 | ReactivedynamicValue3 | I16 | 1 | % | -100 | 100 | RW | For reactive mode 3, the 3rd point power percentage | Installer
2441 | 0989 | ReactiveCos4 | I16 | 0.0001 |  | -10000 | 10000 | RW | For reactive mode 3，the 4th point power factor | Installer
2442 | 098A | ReactivedynamicValue4 | I16 | 1 | % | -100 | 100 | RW | For reactive mode 3, the 4th point power percentage | Installer
2443 | 098B | LockinV | U16 | 1 | % | 0 | 200 | RW | For reactive mode 3，the lochinV voltage percentage | Installer
2444 | 098C | LockoutV | U16 | 1 | % | 0 | 200 | RW | For reactive mode 3，the lochoutV voltage percentage | Installer
2445 | 098D | HighVoltStartValue4 | U16 | 1 | % | 0 | 200 | RW | For reactive mode 4, the percentage of higher voltage start up point | Installer
2446 | 098E | HighVoltEndValue4 | U16 | 1 | % | 0 | 200 | RW | For Reactive mode 4, the percentage of higher voltage ending point | Installer
2447 | 098F | LowVoltStartValue4 | U16 | 1 | % | 0 | 200 | RW | for reactive mode 4 ,the percentage of lower voltage start up point | Installer
2448 | 0990 | LowVoltEndValue4 | U16 | 1 | % | 0 | 200 | RW | For reactive mode 4, the percentage of lower voltage ending point | Installer
2449 | 0991 | LockinPower4 | U16 | 1 | % | 0 | 100 | RW | For reactive mode 4 ，Lockinpower percentage | Installer
2450 | 0992 | LockoutPower4 | U16 | 1 | % | 0 | 100 | RW | For Reactive mode 4，Lockout power percentage | Installer
2451 | 0993 | MaxLeadingReactivePower4 | U16 | 0.01 | %Pn | 0 | 10000 | RW | for Reactive mode 4 , The max reactive power percentage | Installer
2452 | 0994 | ReactiveResponseWaitTime4 | U16 | 10 | ms | 0 | 65535 | RW | For Reactive mode 4, waiting time for reactive power response | Installer
2453 | 0995 | ReactivePowerOffset4 | I16 | 0.01 | %Qmax | -10000 | 10000 | RW | For Reactive mode4, reactive power offset value | Installer
2454 | 0996 | ReactivePowerStart4 | U16 | 0.01 | %Pn | -10000 | 10000 | RW | For reactive mode 4, the percentage of reactive power (higher voltage start point) | Installer
2455 | 0997 | HighVoltStartValue5 | U16 | 1 | % | 0 | 200 | RW | For reactive mode 5, the percentage of higher voltage start up point | Installer
2456 | 0998 | HighVoltEndValue5 | U16 | 1 | % | 0 | 200 | RW | For Reactive mode 5, the percentage of higher voltage ending point | Installer
2457 | 0999 | LowVoltStartValue5 | U16 | 1 | % | 0 | 200 | RW | for reactive mode 5 ,the percentage of lower voltage start up point | Installer
2458 | 099A | LowVoltEndValue5 | U16 | 1 | % | 0 | 200 | RW | For reactive mode 5, the percentage of lower voltage ending point | Installer
2459 | 099B | LockinPower5 | U16 | 1 | % | 0 | 100 | RW | For reactive mode 5 ，Lockinpower percentage | Installer
2460 | 099C | LockoutPower5 | U16 | 1 | % | 0 | 100 | RW | For Reactive mode 5，Lockout power percentage | Installer
2461 | 099D | MaxReactivePower5 | U16 | 0.01 | % | 0 | 10000 | RW | for Reactive mode 5 , The max reactive power percentage | Installer
2462 | 099E | ReactiveResponseWaitTime5 | U16 | 10 | ms | 0 | 65535 | RW | For Reactive mode 5, waiting time for reactive power response | Installer
2463 | 099F | PhaseType | U16 |  |  | 0 | 2 | RW | For Reactive mode 6 ，phase type 0：no Reactive power 1：lagging 2：leading | Installer
2464 | 09A0 | ReactiveResponsePeriod | U16 | 1 | Second | 1 | 65535 | RW | for reactive mode （1、2、3、4、5、6）adjust the time period for reactive power mode | Installer
2465 | 09A1 | MaxLaggingReactivePower4 | U16 | 0.01 | %Pn | 0 | 10000 | RW | Reactive power mode four, the maximum lagging reactive power percentage | Installer
2466 | 09A2
2467 | 09A3
2468 | 09A4
2469 | 09A5
2470 | 09A6
2471 | 09A7
2472 | 09A8
2473 | 09A9
Voltage ride through Parameter (0x09C0-0x09FF)
2496 | 09C0 | VRTConfig | U16 |  |  |  |  | RW | Bit0：LVRT enable bit Bit1：OVRT enable bit Bit2：0 current mode enable bot BIt3：Keep reactive current before VRT Bit8-11：VRT current calculation Mode | Installer
2497 | 09C1 | LvrtInVolt | U16 | 1 | % | 0 | 65535 | RW | The Voltage percentage (start point,LVRT) | Installer
2498 | 09C2 | LvrtFirstPointVolt | U16 | 1 | % | 0 | 65535 | RW | the voltage percentage (1st point, LVRT) | Installer
2499 | 09C3 | LvrtFirstPointTime | U16 | 1 | ms | 0 | 65535 | RW | Time for 1st point ,LVRT | Installer
2500 | 09C4 | LvrtSecondPointVolt | U16 | 1 | % | 0 | 65535 | RW | the voltage percentage (2ND point, LVRT) | Installer
2501 | 09C5 | LvrtSecondPointTime | U16 | 1 | ms | 0 | 65535 | RW | Time for 2nd point ,LVRT | Installer
2502 | 09C6 | LvrtThirdPointVolt | U16 | 1 | % | 0 | 65535 | RW | the voltage percentage (3rd point, LVRT) | Installer
2503 | 09C7 | LvrtThirdPointTime | U16 | 1 | ms | 0 | 65535 | RW | Time for 3rd point ,LVRT | Installer
2504 | 09C8 | LvrtFourthPointVolt | U16 | 1 | % | 0 | 65535 | RW | the voltage percentage (4th point, LVRT) | Installer
2505 | 09C9 | LvrtFourthPointTime | U16 | 1 | ms | 0 | 65535 | RW | Time for 4th point ,LVRT | Installer
2506 | 09CA | LvrtReactiveCurrentCoefficientK | U16 | 0.1 | p.u. | 0 | 65535 | RW | Reactive Current Coefficient (K），LVRT | Installer
2507 | 09CB | LvrtWaitingTimeAfterVoltageRecovery | U16 | 1 | ms | 0 | 65535 | RW | Waiting time after LVRT Recovery | Installer
2508 | 09CC | LvrtPowerBackRate | U16 | 1 | %Pn/min | 1 | 300 | RW | Power reload rate (back from LVRT) | Installer
2509 | 09CD | OvrtInVlot | U16 | 1 | % | 0 | 65535 | RW | The Voltage percentage (start point,OVRT) | Installer
2510 | 09CE | OvrtFirstPointVolt | U16 | 1 | % | 0 | 65535 | RW | the voltage percentage (1st point, OVRT) | Installer
2511 | 09CF | OvrtFirstPointTime | U16 | 10 | ms | 0 | 65535 | RW | Time for 1st point ,OVRT | Installer
2512 | 09D0 | OvrtSecondPointVolt | U16 | 1 | % | 0 | 65535 | RW | the voltage percentage (2ND point, OVRT) | Installer
2513 | 09D1 | OvrtSecondPointTime | U16 | 10 | ms | 0 | 65535 | RW | Time for 2nd point ,OVRT | Installer
2514 | 09D2 | OvrtThirdPointVolt | U16 | 1 | % | 0 | 65535 | RW | the voltage percentage (3rd point, OVRT) | Installer
2515 | 09D3 | OvrtThirdPointTime | U16 | 10 | ms | 0 | 65535 | RW | Time for 3rd point ,OVRT | Installer
2516 | 09D4 | OvrtFourthPointVolt | U16 | 1 | % | 0 | 65535 | RW | the voltage percentage (4th point, OVRT) | Installer
2517 | 09D5 | OvrtFourthPointTime | U16 | 10 | ms | 0 | 65535 | RW | Time for 4th point ,OVRT | Installer
2518 | 09D6 | OvrtReactiveCurrentCoefficientK | U16 | 0.1 | p.u. | 0 | 65535 | RW | Reactive Current Coefficient (K），OVRT | Installer
2519 | 09D7 | OvrtWaitingTimeAfterVoltageRecovery | U16 | 1 | ms | 0 | 65535 | RW | Waiting time after OVRT Recovery | Installer
2520 | 09D8 | OvrtPowerBackRate | U16 | 1 | %Pn/min | 1 | 300 | RW | Power reload rate (back from OVRT) | Installer
2521 | 09D9 | ZeroCurrentModeInLowVolt | U16 | 1 | % | 0 | 65535 | RW | the percentage to low voltage mode from zero current mode | Installer
2522 | 09DA | ZeroCurrentModeInHighVolt | U16 | 1 | % | 0 | 65535 | RW | the percentage to high voltage mode from zero current mode | Installer
2523 | 09DB | LvrtOutVolt | U16 | 1 | % | 0 | 65535 | RW | the voltage percentage for LVRT EXIST | Installer
2524 | 09DC | LvrtIqVoltStart | U16 | 1 | % | 0 | 65535 | RW | The starting point, voltage percentage for reactive current calculation(LVRT) | Installer
2525 | 09DD | OvrtOutVolt | U16 | 1 | % | 0 | 65535 | RW | the voltage percentage for OVRT EXIST | Installer
2526 | 09DE | OvrtIqVoltStart | U16 | 1 | % | 0 | 65535 | RW | The starting point, voltage percentage for reactive current calculation(0VRT) | Installer
islanding、GFCI、ISO Parameter (0x0A00-0x0A3F)
2560 | 0A00 | IslandConfig | U16 |  |  |  |  | RW | Bit0：ISLANDING ENABLE BIT | Installer
2561 | 0A01 | GFCIConfig | U16 |  |  |  |  | RW | Bit0：GFCI enable bit | Installer
2562 | 0A02 | ISOConfig | U16 |  |  |  |  | RW | Bit0：Insulation Resistance testing enable bit Bit1：ground Testing enable bit | Installer
2563 | 0A03 | InsulationProtectionValue | U16 | 1 | kΩ | 30 | 65535 | RW | Insulation resistance Value | Installer
2564 | 0A04 | IsoLeakageCurrentLimit | U16 | 1 | mA | 1 | 50 | RW | leakage current limit , PV to ground | Installer
2565 | 0A05 | GFCILimit | U16 | 1 | mA/kVA | 1 | 50 | RW | Leakage current limit（not to public , can not make change） | Installer
2566 | 0A06
2567 | 0A07
2568 | 0A08
2569 | 0A09
2570 | 0A0A
2571 | 0A0B
2572 | 0A0C
2573 | 0A0D
ARC (0x0A40-0x0A7F)
2624 | 0A40 | [8 empty] | Installer
Paranters setting (0x1000-0x17FF)
Basic Parameter Configuration (0x1000-0x10FF)
4096 | 1000 | AddressMask_Config_Basic1 | U64 |  |  |  |  | R | Each Character in this field, will verify the validity of 64 addresses. Bit4 represents the address where the highest bit address of this field plus 1, 0 means invalid; 1 means valid. | End User
4097 | 1001 | [8 empty] | End User
4098 | 1002 | [8 empty] | End User
4099 | 1003 | [8 empty] | End User
4100 | 1004 | SysTimeConfig_Year | U16 |  | Year | 0 | 99 | RW | System time -year,Actual year=2000+values in Register | End User
4101 | 1005 | SysTimeConfig_Month | U16 |  | Month | 1 | 12 | RW | System time-Month | End User
4102 | 1006 | SysTimeConfig_Date | U16 |  | date | 1 | 31 | RW | System time-Date | End User
4103 | 1007 | SysTimeConfig_Hour | U16 |  | Hour | 0 | 23 | RW | System time -Hour | End User
4104 | 1008 | SysTimeConfig_Minute | U16 |  | Minute | 0 | 59 | RW | System Time -Minutes | End User
4105 | 1009 | SysTimeConfig_Second | U16 |  | Second | 0 | 59 | RW | System Time-Second | End User
4106 | 100A | SysTimeConfig_Control | U16 |  |  | 1 | 1 | RW | Input value is 1, the value of shadow register in system time will upgrade to the real time. It will return to pervious operation status when you read it. 0x0000：success 0x0001：Operating 0xFFFB：Fail,controller refuse to response (controller busy or configuration issue） 0xFFFC：Fail ,Controller no response 0xFFFD：Fail, Current Function Disable 0xFFFE：Fail,Parameter can not be save 0xFFFF：Fail Input Parameters incorrect | End User
4107 | 100B | RS485Config_Address | U16 |  |  | 1 | 247 | RW | RS 485 configuration- communication address | End User
4108 | 100C | RS485Config_Baud | U16 |  |  | 0 | 4 | RW | RS485 Baud Rate Selection 0：4800bps 1：9600bps（Default） 2：19200bps 3：38400bps 4：57600bps | End User
4109 | 100D | RS485Config_StopBit | U16 |  |  | 0 | 2 | RW | RS485Stop bit selection； 0：1bit stop bit（Default） 1：1.5 bit stop bit 2：2bit stop bit | End User
4110 | 100E | RS485Config_ParityBit | U16 |  |  | 0 | 4 | RW | RS485 check bit selection； 0：No Check/None（Default） 1：Even 2：Odd 3：HIgh/Mark 4：Low/Space | End User
4111 | 100F | RS485Config_Control | U16 |  |  | 1 | 1 | RW | Input value is 1, the value of shadow register in system time will upgrade to the real time. It will return to pervious operation status when you read it. 0x0000：success 0x0001：Operating 0xFFFB：Fail,controller refuse to response (controller busy or configuration issue） 0xFFFC：Fail ,Controller no response 0xFFFD：Fail, Current Function Disable 0xFFFE：Fail,Parameter can not be save 0xFFFF：Fail Input Parameters incorrect | End User
4112 | 1010 | PV_InputMode_Config | U16 |  |  | 0 | 1 | RW | PV input Mode Selection 0: Parallel Mode 1:Independent mode | End User
4113 | 1011 | InputType_Channel0_Config | U16 |  |  | 0 | 255 | RW | 0 Type input channel Selection Value "0" mean current input power supply are not available Vale Between "1～127" mean current input power supply by PV； Value between "128~255" mean input power supply by battery； If we got two or more than two values , and all values bogger than 0, it mean input power supply by PV & Battery | End User
4114 | 1012 | InputType_Channel1_Config | U16 |  |  | 0 | 255 | RW |  | Installer
4115 | 1013 | InputType_Channel2_Config | U16 |  |  | 0 | 255 | RW |  | Installer
4116 | 1014 | InputType_Channel3_Config | U16 |  |  | 0 | 255 | RW |  | Installer
4117 | 1015 | InputType_Channel4_Config | U16 |  |  | 0 | 255 | RW |  | Installer
4118 | 1016 | InputType_Channel5_Config | U16 |  |  | 0 | 255 | RW |  | Installer
4119 | 1017 | InputType_Channel6_Config | U16 |  |  | 0 | 255 | RW |  | Installer
4120 | 1018 | InputType_Channel7_Config | U16 |  |  | 0 | 255 | RW |  | Installer
4121 | 1019 | InputType_Channel8_Config | U16 |  |  | 0 | 255 | RW |  | Installer
4122 | 101A | InputType_Channel9_Config | U16 |  |  | 0 | 255 | RW |  | Installer
4123 | 101B | InputType_Channel10_Config | U16 |  |  | 0 | 255 | RW |  | Installer
4124 | 101C | InputType_Channel11_Config | U16 |  |  | 0 | 255 | RW |  | Installer
4125 | 101D | InputType_Channel12_Config | U16 |  |  | 0 | 255 | RW |  | Installer
4126 | 101E | InputType_Channel13_Config | U16 |  |  | 0 | 255 | RW |  | Installer
4127 | 101F | InputType_Channel14_Config | U16 |  |  | 0 | 255 | RW |  | Installer
4128 | 1020 | InputType_Channel15_Config | U16 |  |  | 0 | 255 | RW |  | Installer
4129 | 1021 | InputType_Control | U16 |  |  | 1 | 1 | RW | Input value is 1, the value of shadow register in system time will upgrade to the real time. It will return to pervious operation status when you read it. 0x0000：success 0x0001：Operating 0xFFFB：Fail,controller refuse to response (controller busy or configuration issue） 0xFFFC：Fail ,Controller no response 0xFFFD：Fail, Current Function Disable 0xFFFE：Fail,Parameter can not be save 0xFFFF：Fail Input Parameters incorrect | Installer
4130 | 1022 | SafetyUpdateFromUSB_Control | U16 |  |  | 1 | 1 | RW | Input value is 1, the value of shadow register in system time will upgrade to the real time. It will return to pervious operation status when you read it. 0x0000：success 0x0001：Operating 0xFFFB：Fail,controller refuse to response (controller busy or configuration issue） 0xFFFC：Fail ,Controller no response 0xFFFD：Fail, Current Function Disable 0xFFFE：Fail,Parameter can not be save 0xFFFF：Fail Input Parameters incorrect | Installer
4131 | 1023 | AntiReflux_Control | U16 |  |  | 0 | 2 | RW | Reflux Power control input value 0, disable the reflux power input value 1, power reflux enable with minimum power among the three phase input value 2, power reflux enable with meaning value | Installer
4132 | 1024 | AntiReflux_Power | U16 | 100 | W | 0 | 65535 | RW | Reflux power | Installer
4133 | 1025 | IVCurveScan_Control | U16 |  |  | 0 | 1 | RW | IV curve scan control | Installer
4134 | 1026 | IVCurveScan_Period | U16 | 1 | Minute | 5 | 65535 | RW | Iv Curve scan cycle | Installer
4135 | 1027 | IVCurveScan_Oneshot | U16 |  |  | 1 | 1 | RW | IV curve scan enable, input value 1, enable the I-V curve one time. It will return to pervious operation status when you read it. 0x0000：success 0x0001：Operating 0xFFFB：Fail,controller refuse to response (controller busy or configuration issue） 0xFFFC：Fail ,Controller no response 0xFFFD：Fail, Current Function Disable 0xFFFE：Fail,Parameter can not be save 0xFFFF：Fail Input Parameters incorrect | Installer
4136 | 1028 | IVCurveScan_ReadChannel | U16 |  |  | 0 | 31 | RW | Channel for IV curve scan return value. This register used to specify the PV channel corresponding to the return value of the IV curve scan result. | Installer
4137 | 1029 | EPS_Control | U16 |  |  | 0 | 2 | RW | Emergency Power supply 1: disable emergency power supply 2 enable emergency power supply ,disable cold start 3enable emergency power supply enable cold start | End User
4138 | 102A | EPS_WaitTime | U16 | 1 | Second | 0 | 65535 | RW | Waiting time for emergency power start (Reverse Function) | End User
4139 | 102B | BatteryActive_Control | U16 |  |  | 0 | 1 | RW | Battery automatic activation | End User
4140 | 102C | BatteryActive_Oneshot | U16 |  |  | 1 | 1 | RW | Battery active input value 1, enable the battery active one time. It will return to pervious operation status when you read it. 0x0000：success 0x0001：Operating 0xFFFB：Fail,controller refuse to response (controller busy or configuration issue） 0xFFFC：Fail ,Controller no response 0xFFFD：Fail, Current Function Disable 0xFFFE：Fail,Parameter can not be save 0xFFFF：Fail Input Parameters incorrect | End User
4141 | 102D | CT_Auto_Calibrate | U16 |  |  | 1 | 1 | RW | CT Calibration(Automatic) input value 1, enable the CT calibration one time. It will return to pervious operation status when you read it. 0x0000：success 0x0001：Operating 0xFFFB：Fail,controller refuse to response (controller busy or configuration issue） 0xFFFC：Fail ,Controller no response 0xFFFD：Fail, Current Function Disable 0xFFFE：Fail,Parameter can not be save 0xFFFF：Fail Input Parameters incorrect | Installer
4142 | 102E | Italy_AutoTest | U16 |  |  | 1 | 2 | RW | Italy automatic test Write: Operate standard test; 0x0002: Operate quick test; When reading, return the status of the last write operation: 0x0000: success 0x0001: Standard test is being operated 0x0002: Quick test is being operated 0xFFFB: The operation failed and the controller refused to respond (maybe the controller is busy or the configuration is wrong) 0xFFFC: The operation failed and the controller did not respond 0xFFFD: Operation failed, current function is forbidden 0xFFFE: Operation failed, parameter storage failed 0xFFFF: The operation failed, and the input parameters are incorrect | Installer
4143 | 102F |  | U16 |  |  |  |  | RW |  | Installer
4144 | 1030 | EnergyStatistics_Date_Year | U16 | 1 | Year | 0 | 19 | RW | Register for statistics power return date. This register indicate specifics year of the returned energy data. Year refers to the Nth most recent year relative to the inverter system time. N is the register value. 0: the current year of the system time; 1: 1 year before the system time; 19：19 year before the system time | Installer
4145 | 1031 | EnergyStatistics_Date_Month | U16 | 1 | Month | 1 | 12 | RW | Register for statistics power return date. This register indicate specifics month of the returned energy data | Installer
4146 | 1032 | EnergyStatistics_Date_Date | U16 | 1 | date | 1 | 31 | RW | Register for statistics power return date. This register indicate specifics Day of the returned energy data | Installer
4147 | 1033 | EnergyStatistics_Config | U16 |  |  |  |  | RW | Register for statistics power return date. High byte: the time setting of the returned data. 0x01: Every day, the first 24 data in the return area are valid; 0x02: Every month, the first 31 data in the return area are valid; 0x03: Every year, the first 12 data in the return area are valid; 0x04: life cycle, the first 20 data in the return area are valid; Other: invalid. Low byte: the setting of the returned data. 0x01: photovoltaic generation; 0x02: load consumption; 0x03: electricity Purchased from Grid ; 0x04: electricity sold to grid; 0x05: battery charging power; 0x06: battery discharging power; Other: invalid. | Installer
4148 | 1034 | Language | U16 |  |  | 0 | 65535 | RW | Register for language setting | End User
4149 | 1035 | Parallel_Control | U16 |  |  | 0 | 2 | RW | 0: Disable the inverters' parallel function 1: Enable the inverters' parallel function | Installer
4150 | 1036 | Parallel_Master_Slave | U16 |  |  | 0 | 1 | RW | Configuration 0: Slave 1:Master | Installer
4151 | 1037 | Parallel_Address | U16 |  |  | 0 | 10 | RW | Parallel address | Installer
4152 | 1038 | UnbalancedSupport_Control | U16 |  |  | 0 | 1 | RW | 3-phase 4-wire mode grid unbalanced support control register 0: Disable unbalanced support function (default) 1: Enable unbalanced support function | Installer
4153 | 1039 | PV_Generation_Ratio | U16 | 0.001 | p.u. | 800 | 3600 | RW | Generated power Rate, Default value 1000 | Installer
4154 | 103A | Energy_Purchase_Ratio | U16 | 0.001 | p.u. | 800 | 1500 | RW | Import power Rate, Default Value 1000 | Installer
4155 | 103B | Energy_Selling_Ratio | U16 | 0.001 | p.u. | 800 | 1500 | RW | Export Power Rate, Default Value 1000 | Installer
4156 | 103C | Bat_Charge_Ratio | U16 | 0.001 | p.u. | 800 | 1500 | RW | Battery Charging power Rate, Default Value 1000 | Installer
4157 | 103D | Bat_Discharge_Ratio | U16 | 0.001 | p.u. | 800 | 1500 | RW | Battery Discharging Power, Default Value 1000 | Installer
4158 | 103E
4159 | 103F
4160 | 1040 | AddressMask_Config_Basic2 | U64 |  |  |  |  | R | Each Character in this field, will verify the validity of 64 addresses. Bit4 represents the address where the highest bit address of this field plus 1, 0 means invalid; 1 means valid. | End User
4161 | 1041 | [8 empty] | End User
4162 | 1042 | [8 empty] | End User
4163 | 1043 | [8 empty] | End User
4164 | 1044 | BatConfig_ID | U16 |  |  | 0 | 7 | RW | Battery serial number. The serial number specified by this register corresponds to the battery input interface of the inverter. After successfully writing to this register, the battery parameters will be updated to the parameters corresponding to the written serial number. | End User
4165 | 1045 | BatConfig_Address | U16 |  |  | 0 | 99 | RW | Battery Communication Address, multiple battery connected in the system, this register is used to mark the battery address of the physical interface corresponding to the battery serial number. | End User
4166 | 1046 | BatConfig_Potocol | U16 |  |  | 0 | 65535 | RW | Battery parameter-communication protocol 0: Sofar Built-in BMS 1:Pylontech's Protocol 2： Sofar's Protocol 3：Amass 4:LG 5:Alpha ESS 6.CATL 7.Weco | End User
4167 | 1047 | BatConfig_Voltage_Over | U16 | 0.1 | V | 0 | 65535 | RW | Battery Parameter-Overvoltage protection | Installer
4168 | 1048 | BatConfig_Voltage_Charge | U16 | 0.1 | V | 0 | 65535 | RW | Battery Parameter-Charge voltage protection | Installer
4169 | 1049 | BatConfig_Voltage_Lack | U16 | 0.1 | V | 0 | 65535 | RW | Battery Parameter-undervoltage protection ,lead-acid battery visible | Installer
4170 | 104A | BatConfig_Voltage_Discharge_Stop | U16 | 0.1 | V | 0 | 65535 | RW | Battery Parameter-Lowest discharge voltage | Installer
4171 | 104B | BatConfig_Current_Charge_Limit | U16 | 0.01 | A | 0 | 65535 | RW | Battery Parameter-Maximum charge current limit | End User
4172 | 104C | BatConfig_Current_Discharge_Limit | U16 | 0.01 | A | 0 | 65535 | RW | Battery Parameter-Maximum discharge current limit | End User
4173 | 104D | BatConfig_Depth_of_Discharge | U16 | 1 | % | 1 | 90 | RW | Dod indicates the max discharge power, when SOC<1-DOD, inverter will stop power discharge , inverter will stop power discharge caused by other issues. DOD<=EOD | End User
4174 | 104E | BatConfig_End_of_Discharge | U16 | 1 | % | 1 | 90 | RW | EOD indicate the max discharge power on off grid mode, when SOC<1-EOD, inverter will stop power discharge , inverter will stop power discharge caused by other issues. | End User
4175 | 104F | BatConfig_Capacity | U16 | 1 | Ah | 1 | 65535 | RW | Battery Parameters-Capacity （Default 50） | End User
4176 | 1050 | BatConfig_Voltage_Nominal | U16 | 0.1 | V | 0 | 65535 | RW | Battery Parameters-Rated Battery Voltage (Default 0） | End User
4177 | 1051 | BatConfig_Cell_Type | U16 | 1 |  | 0 | 3 | RW | Battery Parameters_battery Type 0: Lead-acid(Default) 1: lithium iron phosphate Battery 2: Lithium Ternary Battery 3: lithium titanate Battery | End User
4178 | 1052 | BatConfig_EPS_Buffer | U16 | 1 | % | 5 | 100 | RW | Battery parameters-off-grid recovery discharge hysteresis; EPS_Buffer is not greater than EOD | End User
4179 | 1053 | BatConfig_Control | U16 |  |  |  |  | RW | Battery parameters write in control. Input value is 1, the value of shadow register in battery parameters setting will upgrade to System battery parameter configuration .Input value is 2, the value of shadow register in battery parameters setting will upgrade to default value of BatConfig_Potocol . It will return to pervious operation status when you read it. 0x0000：success 0x0001：Operating 0xFFFB：Fail,controller refuse to response (controller busy or configuration issue） 0xFFFC：Fail ,Controller no response 0xFFFD：Fail, Current Function Disable 0xFFFE：Fail,Parameter can not be save 0xFFFF：Fail Input Parameters incorrect | End User
4180 | 1054 | BatConfig_Address2 | U16 |  |  | 0 | 99 | RW | Battery address. If multiple batteries connected in the system, this register used to mark the battery address of the physical interface corresponding to the battery serial number. | End User
4181 | 1055 | BatConfig_Address3 | U16 |  |  | 0 | 99 | RW | Battery address. If multiple batteries connected in the system, this register used to mark the battery address of the physical interface corresponding to the battery serial number. | End User
4182 | 1056 | BatConfig_Address4 | U16 |  |  | 0 | 99 | RW | Battery address. If multiple batteries connected in the system, this register used to mark the battery address of the physical interface corresponding to the battery serial number. | End User
4183 | 1057
4184 | 1058
4185 | 1059
4186 | 105A
4187 | 105B
4188 | 105C
4189 | 105D
4190 | 105E
4191 | 105F
4192 | 1060 | PCCSampleMode | U16 |  |  | 0 | 2 | RW | PCC power acquisition device configuration 0: not used 1: Electricity meter 2: CT 3: ARPC | End User
4193 | 1061 | Resonance_Sensitivity | U16 |  |  | 1 | 100 | RW | Resonance detection sensitivity | End User
4194 | 1062
4195 | 1063
4196 | 1064
4197 | 1065
4198 | 1066
4199 | 1067
4200 | 1068
4201 | 1069
4202 | 106A
4203 | 106B
4204 | 106C
4205 | 106D
4206 | 106E
4207 | 106F
4208 | 1070
4209 | 1071
4210 | 1072
4211 | 1073
4212 | 1074
4213 | 1075
4214 | 1076
4215 | 1077
4216 | 1078
4217 | 1079
4218 | 107A
4219 | 107B
4220 | 107C
4221 | 107D
4222 | 107E
4223 | 107F
4224 | 1080 | AddressMask_Config_Basic3 | U64 |  |  |  |  | R | Each Character in this field, will verify the validity of 64 addresses. Bit4 represents the address where the highest bit address of this field plus 1, 0 means invalid; 1 means valid. | Installer
4225 | 1081 | [8 empty] | Installer
4226 | 1082 | [8 empty] | Installer
4227 | 1083 | [8 empty] | Installer
4228 | 1084 | Arcing_Alarm_Enable | U16 |  |  |  |  | RW | Enable ARC testing | Installer
4229 | 1085 | Arcing_ChannelSelfTest_Comm | U16 |  |  |  |  | RW | written 1 means start self testing(self check all channels)., all cleared after the self -testing | Installer
4230 | 1086 | Arcing_ChannelSelfTest_Result | U32 |  |  |  |  | R | Bit0 represents the self-test result of channel 1, bit1 represents the self-test result of channel 2, bit2 represents the self-test result of channel 3, and bit3 represents the self-test result of channel 4. 1 means self-check failed (or no self-check), 0 means self-check succeeded. " | Installer
4231 | 1087 | [8 empty] | Installer
4232 | 1088 | Arcing_Alarm_Threshold1 | I16 | 1 |  | 0 | 127 | RW | Settable arc alarm threshold (all channels) | Installer
4233 | 1089 | Arcing_Alarm_Threshold2 | I16 | 1 |  | 0 | 127 | RW | Settable arc alarm threshold (all channels) | Installer
4234 | 108A | Arcing_Alarm_Threshold3 | I16 | 1 |  | 0 | 127 | RW | Settable arc alarm threshold (all channels) | Installer
4235 | 108B | Arcing_Alarm_Threshold4 | I16 | 1 |  | 0 | 127 | RW | Settable arc alarm threshold (all channels) | Installer
4236 | 108C | Arcing_Alarm_Clear | U16 |  |  | 0x1234 | 0x1234 | RW | Write in 0x1234 to clear the arc alarm (all channels) | Installer
4237 | 108D | Arcing_Alarm_ShutDown_Threshold | U16 | 1 |  | 1 | 32 | RW | DC arc alarm fault threshold: after "current arc alarm times" is greater than or equal to "current arc alarm times", a DC arc alarm fault is reported and the inverter shuts down | Installer
4238 | 108E | Arcing_Alarm_Counter | U16 | 1 |  | 0 | 32 | R | Current arc alarm times | Installer
4239 | 108F
4240 | 1090
4241 | 1091
4242 | 1092
4243 | 1093
4244 | 1094
4245 | 1095
4246 | 1096
4247 | 1097
4248 | 1098
4249 | 1099
4250 | 109A
4251 | 109B
4252 | 109C
4253 | 109D
4254 | 109E
4255 | 109F
4256 | 10A0 | PLC_Enable_Setting | U16 |  |  |  |  | RW
4257 | 10A1 | PLC_Com_Property | U16 | NULL | NULL | 0 |  | RW | bit0-bot1:0~1 corresponds to 1/1.5 Bit2~bit4:0~7 correspond to three verification methods: NONE/odd/EVEN bit5~bit7 0~3 corresponding to 8/9l two data bit lengths bit8~15 0~7 corresponding to 4800/9600/19200/38400/115200 | End User
4258 | 10A2
4259 | 10A3
4260 | 10A4
4261 | 10A5 | BLE_Enable_Setting | U16 | NULL | NULL | 0 | 1 | RW
4262 | 10A6 | BLE_Com_Property | U16 | NULL | NULL | 0 | 65535 | RW | bit0-bot1:0~1 corresponds to 1/1.5 Bit2~bit4:0~7 correspond to three verification methods: NONE/odd/EVEN bit5~bit7 0~1 corresponding to 8/9l two data bit lengths bit8~15 0~7 corresponding to 4800/9600/19200/38400/115200
4263 | 10A7
4264 | 10A8
4265 | 10A9
4266 | 10AA
4267 | 10AB
4268 | 10AC
4269 | 10AD
4270 | 10AE
4271 | 10AF
4272 | 10B0 | PID_Auto_running_enable | U16 |  |  | 0 | 1 | RW | PID starts to run automatically. 0 means disabled; 1 means enabled. | End User
4273 | 10B1 | PID_Working_Start_Time | BCD16 | 1 | Minute | 0 | 2359 | RW | PID work start time (BCD code). For example: the minimum value 0x0000 means 00:00; The maximum value of 0x2359 means 23:59. | End User
4274 | 10B2 | PID_Working_Hours | U16 | 1 | Minute | 0 | 65535 | RW | PID working hours. | End User
4275 | 10B3 | PID_Working_PV_Threshold | U16 | 0.1 | V | 0 | 65535 | RW | PID starts the PV value threshold. When the PV voltage is lower than the threshold value, PID is allowed to start. | End User
4276 | 10B4 | PID_Break_Restart_Delay | U16 | 1 | Minute | 0 | 65535 | RW | Waiting time for restart after PID fault is closed. | End User
4277 | 10B5
4278 | 10B6
4279 | 10B7
4280 | 10B8
4281 | 10B9
4282 | 10BA
4283 | 10BB
4284 | 10BC
4285 | 10BD
4286 | 10BE
4287 | 10BF
4288 | 10C0
4289 | 10C1
4290 | 10C2
4291 | 10C3
4292 | 10C4
4293 | 10C5
4294 | 10C6
4295 | 10C7
4296 | 10C8
4297 | 10C9
4298 | 10CA
4299 | 10CB
4300 | 10CC
4301 | 10CD
4302 | 10CE
4303 | 10CF
4304 | 10D0
4305 | 10D1
4306 | 10D2
4307 | 10D3
4308 | 10D4
4309 | 10D5
4310 | 10D6
4311 | 10D7
4312 | 10D8
4313 | 10D9
4314 | 10DA
4315 | 10DB
4316 | 10DC
4317 | 10DD
4318 | 10DE
4319 | 10DF
4320 | 10E0
4321 | 10E1
4322 | 10E2
4323 | 10E3
4324 | 10E4
4325 | 10E5
4326 | 10E6
4327 | 10E7
4328 | 10E8
4329 | 10E9
4330 | 10EA
4331 | 10EB
4332 | 10EC
4333 | 10ED
4334 | 10EE
4335 | 10EF
4336 | 10F0
4337 | 10F1
4338 | 10F2
4339 | 10F3
4340 | 10F4
4341 | 10F5
4342 | 10F6
4343 | 10F7
4344 | 10F8
4345 | 10F9
4346 | 10FA
4347 | 10FB
4348 | 10FC
4349 | 10FD
4350 | 10FE
4351 | 10FF
Remote control (0x1100-0x12FF)
4352 | 1100 | AddressMask_Config_Remote1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above and including the address of this field. bit4 represents the address where the highest bit of this field plus 1 is located. 0 means invalid; 1 means valid. | End User
4353 | 1101
4354 | 1102
4355 | 1103
4356 | 1104 | Remote_On_Off_Control | U16 |  |  | 0 | 1 | RW | Remote power on/off. 0x0000: power off 0x0001: power on | End User
4357 | 1105 | Power_Control | U16 |  |  |  |  | RWV | Power control. Bit0: active (address 0x1106) enable bit Bit1: Reactive (address 0x1107-0x1108) enable bit Bit2: Reactive mode selection bit (0: Reactive_Power; 1: Power_Factor) | End User
4358 | 1106 | Active_Power_Export_Limit | U16 | 0.1 | % | 0 | 1000 | RWV | Output maximum active power percentage | End User
4359 | 1107 | Active_Power_Import_Limit | U16 | 0.1 | % | 0 | 1000 | RWV | Input maximum active power percentage | End User
4360 | 1108 | Reactive_Power_Setting | I16 | 0.1 | % | -1000 | 1000 | RWV | Percentage of reactive power. Note: The maximum reactive power is limited by the specific model. | End User
4361 | 1109 | Power_Factor_Setting | I16 | 0.01 | p.u. | -100 | 100 | RWV | Power factor. Note: The minimum power factor is limited by the specific model. | End User
4362 | 110A | Active_Power_Limit_Speed | U16 | 1 | % | 1 | 65535 | RWV | Active power limit change rate | End User
4363 | 110B | Reactive_Power_Response_Time | U16 | 0.1 | second | 0 | 65535 | RWV | Reactive power setting response time | End User
4364 | 110C | [8 empty] | End User
4365 | 110D | [8 empty] | End User
4366 | 110E | [8 empty] | End User
4367 | 110F | [8 empty] | End User
4368 | 1110 | Energy_Storage_Mode_Control | U16 |  |  | 0 | 4 | RW | Energy storage working mode setting; 0: Spontaneous self-use mode 1: Time-of-use electricity price model 2: Timing charging and discharging mode 3: Passive mode 4: Peak clipping mode 5: Off-grid mode Used to change the working mode. | End User
4369 | 1111 | Timing_ID | U16 |  |  | 0 | 3 | RW | Timed charging and discharging-rule number; The smaller the serial number, the higher the priority. After successfully writing to this register, the timing charge and discharge parameters will be updated to the parameters corresponding to the written serial number. | End User
4370 | 1112 | Timing_On_Off_Control | U16 |  |  | 0 | 1 | RW | Timing charge and discharge-enable control; Bit0: charge enable Bit1: Discharge enable | End User
4371 | 1113 | Timing_Charge_Start | U16 | 1 1 | Hour Minute | 0 0 | 23 59 | RW | High byte. Charging start hour Low byte. Charging start minutes | End User
4372 | 1114 | Timing_Charge_End | U16 | 1 1 | Hour Minute | 0 0 | 23 59 | RW | High byte. Charging end hour Low byte. Minutes after charging | End User
4373 | 1115 | Timing_Discharge_Start | U16 | 1 1 | Hour Minute | 0 0 | 23 59 | RW | High byte. Discharge start hour Low byte. Discharge start minute | End User
4374 | 1116 | Timing_Discharge_End | U16 | 1 1 | Hour Minute | 0 0 | 23 59 | RW | High byte. End of discharge hour Low byte. Minutes after discharge | End User
4375 | 1117 | Timing_Power_Charge | U32 | 1 | W | 1 | 4294967296 | RW | Timed charging and discharging-charging power | End User
4376 | 1118 | [8 empty] | End User
4377 | 1119 | Timing_Power_Discharge | U32 | 1 | W | 1 | 4294967296 | RW | Timing charge and discharge-discharge power | End User
4378 | 111A | [8 empty] | End User
4379 | 111B | Timing_Rsvd1 | [6 empty] | Timed charge and discharge-reserved 1 | End User
4380 | 111C | Timing_Rsvd2 | [6 empty] | Timed charge and discharge-reserved 2 | End User
4381 | 111D | Timing_Rsvd3 | [6 empty] | Timed charge and discharge-reserved 3 | End User
4382 | 111E | Timing_Rsvd4 | [6 empty] | Timed charge and discharge-reserved 4 | End User
4383 | 111F | Timing_Control | U16 |  |  | 1 | 1 | RW | Timing charge and discharge write control; When the written value is 1, the value in the shadow register of timing charge and discharge is updated to the system timing charge and discharge configuration; When reading, return the status of the last write operation: 0x0000: success 0x0001: operating 0xFFFB: The operation failed and the controller refused to respond (maybe the controller is busy or the configuration is wrong) 0xFFFC: The operation failed and the controller did not respond 0xFFFD: Operation failed, current function is forbidden 0xFFFE: Operation failed, parameter storage failed 0xFFFF: The operation failed, and the input parameters are incorrect | End User
4384 | 1120 | TOU_ID | U16 |  |  | 0 | 7 | RW | Time-of-use electricity price-rule number; The smaller the serial number, the higher the priority. After successfully writing to this register, the time-of-use electricity price parameter will be updated to the parameter corresponding to the written serial number. | End User
4385 | 1121 | TOU_On_Off_Control | U16 |  |  | 0 | 1 | RW | Time-of-use price-rule enable; 0: disabled 1: enable | End User
4386 | 1122 | TOU_Charge_Start | U16 | 1 1 | Hour Minute | 0 0 | 23 59 | RW | High byte. Charging start hour Low byte. Charging start minutes | End User
4387 | 1123 | TOU_Charge_End | U16 | 1 1 | Hour Minute | 0 0 | 23 59 | RW | High byte. Charging end hour Low byte. Minutes after charging | End User
4388 | 1124 | TOU_Charge_Target_SOC | U16 | 1 | % | 30 | 100 | RW | Time-of-use price-mandatory charging cut-off SOC; The percentage of remaining power. When the current SOC of the battery reaches the value of this register, the forced charging ends and enters the spontaneous self-use mode, while discharging is prohibited. | End User
4389 | 1125 | TOU_Charge_Power | U32 | 1 | W | 1 | 4294967296 | RW | Time-of-use price-mandatory charging power; The set value cannot exceed the rated power of the machine. | End User
4390 | 1126
4391 | 1127 | TOU_Executed_Date_Start | U16 | 1 1 | Month Date | 1 1 | 12 31 | RW | High byte. The month when the rule becomes effective Low byte. Effective date of the rule | End User
4392 | 1128 | TOU_Executed_Date_End | U16 | 1 1 | Month Date | 1 1 | 12 31 | RW | High byte. The month when the rule ceases to take effect Low byte. The date when the rule ceases to take effect | End User
4393 | 1129 | TOU_Executed_Day_of_Week | U16 |  |  |  |  | RW | Time-of-use electricity price-week when the rule takes effect; This register is represented by a bit field, a bit of 0 indicates an invalid day of the week, and a bit of 1 indicates a valid day of the week Bit0: Monday Bit1: Tuesday Bit2: Wednesday Bit3: Thursday Bit4: Friday Bit5: Saturday Bit6: Sunday | Installer
4394 | 112A | TOU_Rsvd1 | [6 empty] | Time-of-use energy price-reserved 1 | End User
4395 | 112B | TOU_Rsvd2 | [6 empty] | Time-of-use energy price-reserved 2 | End User
4396 | 112C | TOU_Rsvd3 | [6 empty] | Time-of-use energy price-reserved 3 | End User
4397 | 112D | TOU_Rsvd4 | [6 empty] | Time-of-use energy price-reserved 4 | End User
4398 | 112E | TOU_Rsvd5 | [6 empty] | Time-of-use energy price-reserved 5 | End User
4399 | 112F | TOU_Control | U16 |  |  | 1 | 1 | RW | Time-of-use energy price-write control; When the written value is 1, the value in the shadow register of the time-of-use electricity price is updated to the system time-of-use electricity price configuration; When reading, return the status of the last write operation: 0x0000: success 0x0001: operating 0xFFFB: The operation failed and the controller refused to respond (maybe the controller is busy or the configuration is wrong) 0xFFFC: The operation failed and the controller did not respond 0xFFFD: Operation failed, current function is forbidden 0xFFFE: Operation failed, parameter storage failed 0xFFFF: The operation failed, and the input parameters are incorrect | End User
4400 | 1130 | Peak_Shaving_Discharge_Threshold | U32 | 1 | W | 100 |  | RW | The power limit that allows the system to buy electricity from the grid | End User
4401 | 1131 | [8 empty] | End User
4402 | 1132 | Peak_Shaving_Charge_Threshold | U32 | 1 | W | 100 |  | RW | The power cap that allows the system to sell electricity to the grid | End User
4403 | 1133 | [8 empty] | End User
4404 | 1134
4405 | 1135
4406 | 1136
4407 | 1137
4408 | 1138
4409 | 1139
4410 | 113A
4411 | 113B
4412 | 113C
4413 | 113D
4414 | 113E
4415 | 113F
4416 | 1140 | AddressMask_Config_Remote2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid. | End User
4417 | 1141
4418 | 1142
4419 | 1143
4420 | 1144 | Off_Grid_Charge_Source | U16 |  |  | 0 | 2 | RW | Off-grid mode-charging source selection: 0: Grid 1: Generator 2: reserved
4421 | 1145 | Off_Grid_Grid_Power | U16 | 0.01 | kW | 0 | 65535 | RW | Off-grid mode-power drawn from the grid
4422 | 1146 | Off_Grid_DG_Power | U16 | 0.01 | kW | 0 | 65535 | RW | Off-grid mode-generator power
4423 | 1147
4424 | 1148
4425 | 1149
4426 | 114A
4427 | 114B
4428 | 114C
4429 | 114D
4430 | 114E
4431 | 114F
4432 | 1150
4433 | 1151
4434 | 1152
4435 | 1153
4436 | 1154
4437 | 1155
4438 | 1156
4439 | 1157
4440 | 1158
4441 | 1159
4442 | 115A
4443 | 115B
4444 | 115C
4445 | 115D
4446 | 115E
4447 | 115F
4448 | 1160
4449 | 1161
4450 | 1162
4451 | 1163
4452 | 1164
4453 | 1165
4454 | 1166
4455 | 1167
4456 | 1168
4457 | 1169
4458 | 116A
4459 | 116B
4460 | 116C
4461 | 116D
4462 | 116E
4463 | 116F
4464 | 1170
4465 | 1171
4466 | 1172
4467 | 1173
4468 | 1174
4469 | 1175
4470 | 1176
4471 | 1177
4472 | 1178
4473 | 1179
4474 | 117A
4475 | 117B
4476 | 117C
4477 | 117D
4478 | 117E
4479 | 117F
4480 | 1180 | AddressMask_Config_Remote3 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid. | End User
4481 | 1181 | [8 empty] | End User
4482 | 1182 | [8 empty] | End User
4483 | 1183 | [8 empty] | End User
4484 | 1184 | Passive_Timeout | U16 | 1 | Second | 0 | 65535 | RW | Passive mode-timeout control; Default value: 0; Set the passive mode communication timeout time. When the inverter does not receive any communication within the time set by this register, the inverter will force the timeout action. In particular, writing 0 to this register will disable the timeout function. | End User
4485 | 1185 | Passive_Timeout_Action | U16 |  |  | 0 | 1 | RW | Passive mode-timeout action; 0: Forced standby 1: Forced to restore to the energy storage mode before entering the passive mode | End User
4486 | 1186 | Passive_Rsvd1 | [6 empty] | Passive mode-reserved 1 | End User
4487 | 1187 | Passive_Manual_Gdes | I32 | 1 | W | -2147483648 | 2147483647 | RW | Manual mode expected grid power (Gdes); A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
4488 | 1188 | [8 empty] | End User
4489 | 1189 | Passive_Manual_Blo | I32 | 1 | W | -2147483648 | 2147483647 | RW | The minimum charge and discharge power of the battery in Manual mode (Blo); Positive value means charging; Negative values indicate discharge. | End User
4490 | 118A | [8 empty] | End User
4491 | 118B | Passive_Manual_Bup | I32 | 1 | W | -2147483648 | 2147483647 | RW | The maximum charge and discharge power of the battery in Manual mode (Bup); Positive value means charging; Negative values indicate discharge. | End User
4492 | 118C | [8 empty] | End User
4493 | 118D | Passive_Manual_Gdzup | I32 | 1 | W | -2147483648 | 2147483647 | RW | Manual mode allows selling electric power (Gdzup); A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
4494 | 118E | [8 empty] | End User
4495 | 118F | Passive_Manual_Gdzlo | I32 | 1 | W | -2147483648 | 2147483647 | RW | Manual mode allows to buy electric power (Gdzlo); A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
4496 | 1190 | [8 empty] | End User
4497 | 1191 | Passive_Scheduler_Gdes_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode expected grid power (Gdes_Ante); The parameters of the planned task are valid during the planned time period. A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
4498 | 1192 | [8 empty] | End User
4499 | 1193 | Passive_Scheduler_Blo_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | The minimum charge and discharge power of the battery in Scheduler mode (Blo_Ante); The parameters of the planned task are valid during the planned time period. A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
4500 | 1194 | [8 empty] | End User
4501 | 1195 | Passive_Scheduler_Bup_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | The maximum charge and discharge power of the battery in Scheduler mode (Bup_Ante); The parameters of the planned task are valid during the planned time period. A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
4502 | 1196 | [8 empty] | End User
4503 | 1197 | Passive_Scheduler_Gdzup_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode allows to sell electric power (Gdzup_Ante); The parameters of the planned task are valid during the planned time period. A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
4504 | 1198 | [8 empty] | End User
4505 | 1199 | Passive_Scheduler_Gdzlo_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode allows to buy electric power (Gdzlo_Ante); The parameters of the planned task are valid during the planned time period. A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
4506 | 119A | [8 empty] | End User
4507 | 119B | Passive_Scheduler_Gdes_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode expected grid power (Gdes_Post); Schedule task parameters, valid after the scheduled time period. A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
4508 | 119C | [8 empty] | End User
4509 | 119D | Passive_Scheduler_Blo_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | The minimum charge and discharge power of the battery in Scheduler mode (Blo_Post); Schedule task parameters, valid after the scheduled time period. A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
4510 | 119E | [8 empty] | End User
4511 | 119F | Passive_Scheduler_Bup_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | The maximum charge and discharge power of the battery in Scheduler mode (Bup_Post); Schedule task parameters, valid after the scheduled time period. A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
4512 | 11A0 | [8 empty] | End User
4513 | 11A1 | Passive_Scheduler_Gdzup_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode allows to sell electric power (Gdzup_Post); Schedule task parameters, valid after the scheduled time period. A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
4514 | 11A2 | [8 empty] | End User
4515 | 11A3 | Passive_Scheduler_Gdzlo_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode allows to buy electric power (Gdzlo_Post); Schedule task parameters, valid after the scheduled time period. A positive value indicates the power direction "from the grid to the system"; Negative values indicate the power direction "from system to grid". | End User
4516 | 11A4 | [8 empty] | End User
4517 | 11A5 | Passive_Scheduler_StartTime | U32 | 1 | Second | 0 | 4294967296 | RW | Scheduler mode application expectation parameter setting value start time; StartTime is in unix time format. Since the internal time of the system defaults to Greenwich Mean Time (GMT), when setting this parameter, you should pay attention to the local time zone of your country, StartTime=(local Unix Time)±(local time and UTC/GMT The number of seconds corresponding to the time difference) | End User
4518 | 11A6 | [8 empty] | End User
4519 | 11A7 | Passive_Scheduler_DurationTime | U32 | 1 | Second | 0 | 4294967296 | RW | Scheduler mode application expects the duration of the parameter setting value (DurationTime) | End User
4520 | 11A8 | [8 empty] | End User
4521 | 11A9 | Passive_Scheduler_ManagementMode | U16 |  |  | 0 | 2 | RW | Scheduler mode management mode selection (ManagementMode); 0: Spontaneous self-use mode 1: Manual mode 2: Scheduler mode Only 0, 1, 2 can be input, other data is invalid. | End User
4522 | 11AA
4523 | 11AB
4524 | 11AC
4525 | 11AD
4526 | 11AE
4527 | 11AF
4528 | 11B0
4529 | 11B1
4530 | 11B2
4531 | 11B3
4532 | 11B4
4533 | 11B5
4534 | 11B6
4535 | 11B7
4536 | 11B8
4537 | 11B9
4538 | 11BA
4539 | 11BB
4540 | 11BC
4541 | 11BD
4542 | 11BE
4543 | 11BF
4544 | 11C0 | AddressMask_Config_Remote4 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid. | End User
4545 | 11C1 | [8 empty] | End User
4546 | 11C2 | [8 empty] | End User
4547 | 11C3 | [8 empty] | End User
4548 | 11C4
4549 | 11C5
The inverter returns a read-only result (0x1300-0x15FF)
4864 | 1300 | AddressMask_Config_ReadOnly_Result1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid.
4865 | 1301
4866 | 1302
4867 | 1303
4868 | 1304 | Italay_Autotest_Result1 | U16 | 0.1 | V |  |  | R | Italian automatic test 59.s1. The first-level overvoltage protection value is set by default.
4869 | 1305 | Italay_Autotest_Result2 | U16 | 1 | ms |  |  | R | Italian automatic test 59.s1. The first-level overvoltage protection time is set by default.
4870 | 1306 | Italay_Autotest_Result3 | U16 | 0.1 | V |  |  | R | Italian automatic test 59.s1. Test result of level 1 overvoltage protection value.
4871 | 1307 | Italay_Autotest_Result4 | U16 | 1 | ms |  |  | R | Italian automatic test 59.s1. The first level overvoltage protection time test result.
4872 | 1308 | Italay_Autotest_Result5 | U16 | 0.1 | V |  |  | R | Italian automatic test 59.s2. The secondary overvoltage protection value is set by default.
4873 | 1309 | Italay_Autotest_Result6 | U16 | 1 | ms |  |  | R | Italian automatic test 59.s2. The second-level overvoltage protection time is set by default.
4874 | 130A | Italay_Autotest_Result7 | U16 | 0.1 | V |  |  | R | Italian automatic test 59.s2. Test result of secondary overvoltage protection value.
4875 | 130B | Italay_Autotest_Result8 | U16 | 1 | ms |  |  | R | Italian automatic test 59.s2. Test result of secondary overvoltage protection time.
4876 | 130C | Italay_Autotest_Result9 | U16 | 0.1 | V |  |  | R | Italian automatic test 27.s1. The first-level undervoltage protection value is set by default.
4877 | 130D | Italay_Autotest_Result10 | U16 | 1 | ms |  |  | R | Italian automatic test 27.s1. The first-level undervoltage protection time is set by default.
4878 | 130E | Italay_Autotest_Result11 | U16 | 0.1 | V |  |  | R | Italian automatic test 27.s1. The first level undervoltage protection value test result.
4879 | 130F | Italay_Autotest_Result12 | U16 | 1 | ms |  |  | R | Italian automatic test 27.s1. The first level undervoltage protection time test result.
4880 | 1310 | Italay_Autotest_Result13 | U16 | 0.1 | V |  |  | R | Italian automatic test 27.s2. The secondary undervoltage protection value is set by default.
4881 | 1311 | Italay_Autotest_Result14 | U16 | 1 | ms |  |  | R | Italian automatic test 27.s2. The second level undervoltage protection time is set by default.
4882 | 1312 | Italay_Autotest_Result15 | U16 | 0.1 | V |  |  | R | Italian automatic test 27.s2. Test result of secondary undervoltage protection value.
4883 | 1313 | Italay_Autotest_Result16 | U16 | 1 | ms |  |  | R | Italian automatic test 27.s2. Test result of secondary undervoltage protection time.
4884 | 1314 | Italay_Autotest_Result17 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81>s1. The first-level over-frequency protection value is set by default.
4885 | 1315 | Italay_Autotest_Result18 | U16 | 1 | ms |  |  | R | Italian automatic test 81>s1. The first-level over-frequency protection time is set by default.
4886 | 1316 | Italay_Autotest_Result19 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81>s1. Test result of level 1 over-frequency protection value.
4887 | 1317 | Italay_Autotest_Result20 | U16 | 1 | ms |  |  | R | Italian automatic test 81>s1. The first level over-frequency protection time test result.
4888 | 1318 | Italay_Autotest_Result21 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81>s2. The second-level over-frequency protection value is set by default.
4889 | 1319 | Italay_Autotest_Result22 | U16 | 1 | ms |  |  | R | Italian automatic test 81>s2. The second level over-frequency protection time is set by default.
4890 | 131A | Italay_Autotest_Result23 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81>s2. Test result of secondary over-frequency protection value.
4891 | 131B | Italay_Autotest_Result24 | U16 | 1 | ms |  |  | R | Italian automatic test 81>s2. Test result of secondary over-frequency protection time.
4892 | 131C | Italay_Autotest_Result25 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81<s1. The first level under-frequency protection value is set by default.
4893 | 131D | Italay_Autotest_Result26 | U16 | 1 | ms |  |  | R | Italian automatic test 81<s1. The first level under-frequency protection time is set by default.
4894 | 131E | Italay_Autotest_Result27 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81<s1. Test result of first-level under-frequency protection value.
4895 | 131F | Italay_Autotest_Result28 | U16 | 1 | ms |  |  | R | Italian automatic test 81<s1. The first level under-frequency protection time test result.
4896 | 1320 | Italay_Autotest_Result29 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81<s2. The second-level under-frequency protection value is set by default.
4897 | 1321 | Italay_Autotest_Result30 | U16 | 1 | ms |  |  | R | Italian automatic test 81<s2. The second level under-frequency protection time is set by default.
4898 | 1322 | Italay_Autotest_Result31 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81<s2. Test result of secondary underfrequency protection value.
4899 | 1323 | Italay_Autotest_Result32 | U16 | 1 | ms |  |  | R | Italian automatic test 81<s2. Test result of secondary under-frequency protection time.
4900 | 1324 | Italay_Autotest_Result33 | [6 empty] | Italy automatic test result 33
4901 | 1325 | Italay_Autotest_Result34 | [6 empty] | Italy automatic test result 34
4902 | 1326 | Italay_Autotest_Result35 | [6 empty] | Italy automatic test result 35
4903 | 1327 | Italay_Autotest_Result36 | [6 empty] | Italy automatic test result 36
4904 | 1328 | Italay_Autotest_Result37 | [6 empty] | Italy automatic test result 37
4905 | 1329 | Italay_Autotest_Result38 | [6 empty] | Italy automatic test result 38
4906 | 132A | Italay_Autotest_Result39 | [6 empty] | Italy automatic test result 39
4907 | 132B | Italay_Autotest_Result40 | [6 empty] | Italian automatic test result 40
4908 | 132C | Italay_Autotest_Result41 | [6 empty] | Italian automatic test result 41
4909 | 132D | Italay_Autotest_Result42 | [6 empty] | Italian automatic test result 42
4910 | 132E | Italay_Autotest_Result43 | [6 empty] | Italy automatic test result 43
4911 | 132F | Italay_Autotest_Result44 | [6 empty] | Italy automatic test result 44
4912 | 1330 | Italay_Autotest_Result45 | [6 empty] | Italy automatic test result 45
4913 | 1331 | Italay_Autotest_Result46 | [6 empty] | Italy automatic test result 46
4914 | 1332 | Italay_Autotest_Result47 | [6 empty] | Italy automatic test result 47
4915 | 1333 | Italay_Autotest_Result48 | [6 empty] | Italy automatic test result 48
0
4928 | 1340 | AddressMask_Config_ReadOnly_Result2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid.
4929 | 1341
4930 | 1342
4931 | 1343
4932 | 1344 | IVCurve_Voltage1 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 1
4933 | 1345 | IVCurve_Current1 | U16 | 0.01 | A |  |  | R | IV curve sweep current 1
4934 | 1346 | IVCurve_Voltage2 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 2
4935 | 1347 | IVCurve_Current2 | U16 | 0.01 | A |  |  | R | IV curve scan current 2
4936 | 1348 | IVCurve_Voltage3 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 3
4937 | 1349 | IVCurve_Current3 | U16 | 0.01 | A |  |  | R | IV curve scan current 3
4938 | 134A | IVCurve_Voltage4 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 4
4939 | 134B | IVCurve_Current4 | U16 | 0.01 | A |  |  | R | IV curve scan current 4
4940 | 134C | IVCurve_Voltage5 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 5
4941 | 134D | IVCurve_Current5 | U16 | 0.01 | A |  |  | R | IV curve scan current 5
4942 | 134E | IVCurve_Voltage6 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 6
4943 | 134F | IVCurve_Current6 | U16 | 0.01 | A |  |  | R | IV curve scan current 6
4944 | 1350 | IVCurve_Voltage7 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 7
4945 | 1351 | IVCurve_Current7 | U16 | 0.01 | A |  |  | R | IV curve scan current 7
4946 | 1352 | IVCurve_Voltage8 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 8
4947 | 1353 | IVCurve_Current8 | U16 | 0.01 | A |  |  | R | IV curve scan current 8
4948 | 1354 | IVCurve_Voltage9 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 9
4949 | 1355 | IVCurve_Current9 | U16 | 0.01 | A |  |  | R | IV curve sweep current 9
4950 | 1356 | IVCurve_Voltage10 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 10
4951 | 1357 | IVCurve_Current10 | U16 | 0.01 | A |  |  | R | IV curve sweep current 10
4952 | 1358 | IVCurve_Voltage11 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 11
4953 | 1359 | IVCurve_Current11 | U16 | 0.01 | A |  |  | R | IV curve scan current 11
4954 | 135A | IVCurve_Voltage12 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 12
4955 | 135B | IVCurve_Current12 | U16 | 0.01 | A |  |  | R | IV curve scan current 12
4956 | 135C | IVCurve_Voltage13 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 13
4957 | 135D | IVCurve_Current13 | U16 | 0.01 | A |  |  | R | IV curve sweep current 13
4958 | 135E | IVCurve_Voltage14 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 14
4959 | 135F | IVCurve_Current14 | U16 | 0.01 | A |  |  | R | IV curve scan current 14
4960 | 1360 | IVCurve_Voltage15 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 15
4961 | 1361 | IVCurve_Current15 | U16 | 0.01 | A |  |  | R | IV curve scan current 15
4962 | 1362 | IVCurve_Voltage16 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 16
4963 | 1363 | IVCurve_Current16 | U16 | 0.01 | A |  |  | R | IV curve scan current 16
4964 | 1364 | IVCurve_Voltage17 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 17
4965 | 1365 | IVCurve_Current17 | U16 | 0.01 | A |  |  | R | IV curve scan current 17
4966 | 1366 | IVCurve_Voltage18 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 18
4967 | 1367 | IVCurve_Current18 | U16 | 0.01 | A |  |  | R | IV curve scan current 18
4968 | 1368 | IVCurve_Voltage19 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 19
4969 | 1369 | IVCurve_Current19 | U16 | 0.01 | A |  |  | R | IV curve scan current 19
4970 | 136A | IVCurve_Voltage20 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 20
4971 | 136B | IVCurve_Current20 | U16 | 0.01 | A |  |  | R | IV curve scan current 20
4972 | 136C | IVCurve_Voltage21 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 21
4973 | 136D | IVCurve_Current21 | U16 | 0.01 | A |  |  | R | IV curve scan current 21
4974 | 136E | IVCurve_Voltage22 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 22
4975 | 136F | IVCurve_Current22 | U16 | 0.01 | A |  |  | R | IV curve scan current 22
4976 | 1370 | IVCurve_Voltage23 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 23
4977 | 1371 | IVCurve_Current23 | U16 | 0.01 | A |  |  | R | IV curve scan current 23
4978 | 1372 | IVCurve_Voltage24 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 24
4979 | 1373 | IVCurve_Current24 | U16 | 0.01 | A |  |  | R | IV curve scan current 24
4980 | 1374 | IVCurve_Voltage25 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 25
4981 | 1375 | IVCurve_Current25 | U16 | 0.01 | A |  |  | R | IV curve scan current 25
4982 | 1376 | IVCurve_Voltage26 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 26
4983 | 1377 | IVCurve_Current26 | U16 | 0.01 | A |  |  | R | IV curve scan current 26
4984 | 1378 | IVCurve_Voltage27 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 27
4985 | 1379 | IVCurve_Current27 | U16 | 0.01 | A |  |  | R | IV curve scan current 27
4986 | 137A | IVCurve_Voltage28 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 28
4987 | 137B | IVCurve_Current28 | U16 | 0.01 | A |  |  | R | IV curve scan current 28
4988 | 137C | IVCurve_Voltage29 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 29
4989 | 137D | IVCurve_Current29 | U16 | 0.01 | A |  |  | R | IV curve scan current 29
4990 | 137E | IVCurve_Voltage30 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 30
4991 | 137F | IVCurve_Current30 | U16 | 0.01 | A |  |  | R | IV curve scan current 30
4992 | 1380 | AddressMask_Config_ReadOnly_Result3 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid
4993 | 1381
4994 | 1382
4995 | 1383
4996 | 1384 | IVCurve_Voltage31 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 31
4997 | 1385 | IVCurve_Current31 | U16 | 0.01 | A |  |  | R | IV curve scan current 31
4998 | 1386 | IVCurve_Voltage32 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 32
4999 | 1387 | IVCurve_Current32 | U16 | 0.01 | A |  |  | R | IV curve scan current 32
5000 | 1388 | IVCurve_Voltage33 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 33
5001 | 1389 | IVCurve_Current33 | U16 | 0.01 | A |  |  | R | IV curve scan current 33
5002 | 138A | IVCurve_Voltage34 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 34
5003 | 138B | IVCurve_Current34 | U16 | 0.01 | A |  |  | R | IV curve scan current 34
5004 | 138C | IVCurve_Voltage35 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 35
5005 | 138D | IVCurve_Current35 | U16 | 0.01 | A |  |  | R | IV curve scan current 35
5006 | 138E | IVCurve_Voltage36 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 36
5007 | 138F | IVCurve_Current36 | U16 | 0.01 | A |  |  | R | IV curve scan current 36
5008 | 1390 | IVCurve_Voltage37 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 37
5009 | 1391 | IVCurve_Current37 | U16 | 0.01 | A |  |  | R | IV curve scan current 37
5010 | 1392 | IVCurve_Voltage38 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 38
5011 | 1393 | IVCurve_Current38 | U16 | 0.01 | A |  |  | R | IV curve scan current 38
5012 | 1394 | IVCurve_Voltage39 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 39
5013 | 1395 | IVCurve_Current39 | U16 | 0.01 | A |  |  | R | IV curve scan current 39
5014 | 1396 | IVCurve_Voltage40 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 40
5015 | 1397 | IVCurve_Current40 | U16 | 0.01 | A |  |  | R | IV curve scan current 40
5016 | 1398 | IVCurve_Voltage41 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 41
5017 | 1399 | IVCurve_Current41 | U16 | 0.01 | A |  |  | R | IV curve scan current 41
5018 | 139A | IVCurve_Voltage42 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 42
5019 | 139B | IVCurve_Current42 | U16 | 0.01 | A |  |  | R | IV curve scan current 42
5020 | 139C | IVCurve_Voltage43 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 43
5021 | 139D | IVCurve_Current43 | U16 | 0.01 | A |  |  | R | IV curve scan current 43
5022 | 139E | IVCurve_Voltage44 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 44
5023 | 139F | IVCurve_Current44 | U16 | 0.01 | A |  |  | R | IV curve scan current 44
5024 | 13A0 | IVCurve_Voltage45 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 45
5025 | 13A1 | IVCurve_Current45 | U16 | 0.01 | A |  |  | R | IV curve scan current 45
5026 | 13A2 | IVCurve_Voltage46 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 46
5027 | 13A3 | IVCurve_Current46 | U16 | 0.01 | A |  |  | R | IV curve scan current 46
5028 | 13A4 | IVCurve_Voltage47 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 47
5029 | 13A5 | IVCurve_Current47 | U16 | 0.01 | A |  |  | R | IV curve scan current 47
5030 | 13A6 | IVCurve_Voltage48 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 48
5031 | 13A7 | IVCurve_Current48 | U16 | 0.01 | A |  |  | R | IV curve scan current 48
5032 | 13A8 | IVCurve_Voltage49 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 49
5033 | 13A9 | IVCurve_Current49 | U16 | 0.01 | A |  |  | R | IV curve scan current 49
5034 | 13AA | IVCurve_Voltage50 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 50
5035 | 13AB | IVCurve_Current50 | U16 | 0.01 | A |  |  | R | IV curve scan current 50
5036 | 13AC | IVCurve_Voltage51 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 51
5037 | 13AD | IVCurve_Current51 | U16 | 0.01 | A |  |  | R | IV curve scan current 51
5038 | 13AE | IVCurve_Voltage52 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 52
5039 | 13AF | IVCurve_Current52 | U16 | 0.01 | A |  |  | R | IV curve scan current 52
5040 | 13B0 | IVCurve_Voltage53 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 53
5041 | 13B1 | IVCurve_Current53 | U16 | 0.01 | A |  |  | R | IV curve scan current 53
5042 | 13B2 | IVCurve_Voltage54 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 54
5043 | 13B3 | IVCurve_Current54 | U16 | 0.01 | A |  |  | R | IV curve scan current 54
5044 | 13B4 | IVCurve_Voltage55 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 55
5045 | 13B5 | IVCurve_Current55 | U16 | 0.01 | A |  |  | R | IV curve scan current 55
5046 | 13B6 | IVCurve_Voltage56 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 56
5047 | 13B7 | IVCurve_Current56 | U16 | 0.01 | A |  |  | R | IV curve scan current 56
5048 | 13B8 | IVCurve_Voltage57 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 57
5049 | 13B9 | IVCurve_Current57 | U16 | 0.01 | A |  |  | R | IV curve scan current 57
5050 | 13BA | IVCurve_Voltage58 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 58
5051 | 13BB | IVCurve_Current58 | U16 | 0.01 | A |  |  | R | IV curve scan current 58
5052 | 13BC | IVCurve_Voltage59 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 59
5053 | 13BD | IVCurve_Current59 | U16 | 0.01 | A |  |  | R | IV curve scan current 59
5054 | 13BE | IVCurve_Voltage60 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 60
5055 | 13BF | IVCurve_Current60 | U16 | 0.01 | A |  |  | R | IV curve scan current 60
5056 | 13C0 | AddressMask_Config_ReadOnly_Result4 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid
5057 | 13C1
5058 | 13C2
5059 | 13C3
5060 | 13C4 | IVCurve_Voltage61 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 61
5061 | 13C5 | IVCurve_Current61 | U16 | 0.01 | A |  |  | R | IV curve scan current 61
5062 | 13C6 | IVCurve_Voltage62 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 62
5063 | 13C7 | IVCurve_Current62 | U16 | 0.01 | A |  |  | R | IV curve scan current 62
5064 | 13C8 | IVCurve_Voltage63 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 63
5065 | 13C9 | IVCurve_Current63 | U16 | 0.01 | A |  |  | R | IV curve scan current 63
5066 | 13CA | IVCurve_Voltage64 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 64
5067 | 13CB | IVCurve_Current64 | U16 | 0.01 | A |  |  | R | IV curve scan current 64
5068 | 13CC | IVCurve_Voltage65 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 65
5069 | 13CD | IVCurve_Current65 | U16 | 0.01 | A |  |  | R | IV curve scan current 65
5070 | 13CE | IVCurve_Voltage66 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 66
5071 | 13CF | IVCurve_Current66 | U16 | 0.01 | A |  |  | R | IV curve scan current 66
5072 | 13D0 | IVCurve_Voltage67 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 67
5073 | 13D1 | IVCurve_Current67 | U16 | 0.01 | A |  |  | R | IV curve scan current 67
5074 | 13D2 | IVCurve_Voltage68 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 68
5075 | 13D3 | IVCurve_Current68 | U16 | 0.01 | A |  |  | R | IV curve scan current 68
5076 | 13D4 | IVCurve_Voltage69 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 69
5077 | 13D5 | IVCurve_Current69 | U16 | 0.01 | A |  |  | R | IV curve scan current 69
5078 | 13D6 | IVCurve_Voltage70 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 70
5079 | 13D7 | IVCurve_Current70 | U16 | 0.01 | A |  |  | R | IV curve scan current 70
5080 | 13D8 | IVCurve_Voltage71 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 71
5081 | 13D9 | IVCurve_Current71 | U16 | 0.01 | A |  |  | R | IV curve scan current 71
5082 | 13DA | IVCurve_Voltage72 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 72
5083 | 13DB | IVCurve_Current72 | U16 | 0.01 | A |  |  | R | IV curve scan current 72
5084 | 13DC | IVCurve_Voltage73 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 73
5085 | 13DD | IVCurve_Current73 | U16 | 0.01 | A |  |  | R | IV curve scan current 73
5086 | 13DE | IVCurve_Voltage74 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 74
5087 | 13DF | IVCurve_Current74 | U16 | 0.01 | A |  |  | R | IV curve scan current 74
5088 | 13E0 | IVCurve_Voltage75 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 75
5089 | 13E1 | IVCurve_Current75 | U16 | 0.01 | A |  |  | R | IV curve scan current 75
5090 | 13E2 | IVCurve_Voltage76 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 76
5091 | 13E3 | IVCurve_Current76 | U16 | 0.01 | A |  |  | R | IV curve scan current 76
5092 | 13E4 | IVCurve_Voltage77 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 77
5093 | 13E5 | IVCurve_Current77 | U16 | 0.01 | A |  |  | R | IV curve scan current 77
5094 | 13E6 | IVCurve_Voltage78 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 78
5095 | 13E7 | IVCurve_Current78 | U16 | 0.01 | A |  |  | R | IV curve sweep current 78
5096 | 13E8 | IVCurve_Voltage79 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 79
5097 | 13E9 | IVCurve_Current79 | U16 | 0.01 | A |  |  | R | IV curve sweep current 79
5098 | 13EA | IVCurve_Voltage80 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 80
5099 | 13EB | IVCurve_Current80 | U16 | 0.01 | A |  |  | R | IV curve sweep current 80
5100 | 13EC | IVCurve_Voltage81 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 81
5101 | 13ED | IVCurve_Current81 | U16 | 0.01 | A |  |  | R | IV curve sweep current 81
5102 | 13EE | IVCurve_Voltage82 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 82
5103 | 13EF | IVCurve_Current82 | U16 | 0.01 | A |  |  | R | IV curve scan current 82
5104 | 13F0 | IVCurve_Voltage83 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 83
5105 | 13F1 | IVCurve_Current83 | U16 | 0.01 | A |  |  | R | IV curve sweep current 83
5106 | 13F2 | IVCurve_Voltage84 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 84
5107 | 13F3 | IVCurve_Current84 | U16 | 0.01 | A |  |  | R | IV curve sweep current 84
5108 | 13F4 | IVCurve_Voltage85 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 85
5109 | 13F5 | IVCurve_Current85 | U16 | 0.01 | A |  |  | R | IV curve sweep current 85
5110 | 13F6 | IVCurve_Voltage86 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 86
5111 | 13F7 | IVCurve_Current86 | U16 | 0.01 | A |  |  | R | IV curve scan current 86
5112 | 13F8 | IVCurve_Voltage87 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 87
5113 | 13F9 | IVCurve_Current87 | U16 | 0.01 | A |  |  | R | IV curve scan current 87
5114 | 13FA | IVCurve_Voltage88 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 88
5115 | 13FB | IVCurve_Current88 | U16 | 0.01 | A |  |  | R | IV curve sweep current 88
5116 | 13FC | IVCurve_Voltage89 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 89
5117 | 13FD | IVCurve_Current89 | U16 | 0.01 | A |  |  | R | IV curve scan current 89
5118 | 13FE | IVCurve_Voltage90 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 90
5119 | 13FF | IVCurve_Current90 | U16 | 0.01 | A |  |  | R | IV curve sweep current 90
5120 | 1400 | AddressMask_Config_ReadOnly_Result5 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid.
5121 | 1401
5122 | 1402
5123 | 1403
5124 | 1404 | IVCurve_Voltage91 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 91
5125 | 1405 | IVCurve_Current91 | U16 | 0.01 | A |  |  | R | IV curve sweep current 91
5126 | 1406 | IVCurve_Voltage92 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 92
5127 | 1407 | IVCurve_Current92 | U16 | 0.01 | A |  |  | R | IV curve scan current 92
5128 | 1408 | IVCurve_Voltage93 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 93
5129 | 1409 | IVCurve_Current93 | U16 | 0.01 | A |  |  | R | IV curve sweep current 93
5130 | 140A | IVCurve_Voltage94 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 94
5131 | 140B | IVCurve_Current94 | U16 | 0.01 | A |  |  | R | IV curve scan current 94
5132 | 140C | IVCurve_Voltage95 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 95
5133 | 140D | IVCurve_Current95 | U16 | 0.01 | A |  |  | R | IV curve sweep current 95
5134 | 140E | IVCurve_Voltage96 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 96
5135 | 140F | IVCurve_Current96 | U16 | 0.01 | A |  |  | R | IV curve scan current 96
5136 | 1410 | IVCurve_Voltage97 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 97
5137 | 1411 | IVCurve_Current97 | U16 | 0.01 | A |  |  | R | IV curve scan current 97
5138 | 1412 | IVCurve_Voltage98 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 98
5139 | 1413 | IVCurve_Current98 | U16 | 0.01 | A |  |  | R | IV curve scan current 98
5140 | 1414 | IVCurve_Voltage99 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 99
5141 | 1415 | IVCurve_Current99 | U16 | 0.01 | A |  |  | R | IV curve sweep current 99
5142 | 1416 | IVCurve_Voltage100 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 100
5143 | 1417 | IVCurve_Current100 | U16 | 0.01 | A |  |  | R | IV curve sweep current 100
5144 | 1418 | IVCurve_Voltage101 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 101
5145 | 1419 | IVCurve_Current101 | U16 | 0.01 | A |  |  | R | IV curve sweep current 101
5146 | 141A | IVCurve_Voltage102 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 102
5147 | 141B | IVCurve_Current102 | U16 | 0.01 | A |  |  | R | IV curve scan current 102
5148 | 141C | IVCurve_Voltage103 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 103
5149 | 141D | IVCurve_Current103 | U16 | 0.01 | A |  |  | R | IV curve scan current 103
5150 | 141E | IVCurve_Voltage104 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 104
5151 | 141F | IVCurve_Current104 | U16 | 0.01 | A |  |  | R | IV curve scan current 104
5152 | 1420 | IVCurve_Voltage105 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 105
5153 | 1421 | IVCurve_Current105 | U16 | 0.01 | A |  |  | R | IV curve scan current 105
5154 | 1422 | IVCurve_Voltage106 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 106
5155 | 1423 | IVCurve_Current106 | U16 | 0.01 | A |  |  | R | IV curve scan current 106
5156 | 1424 | IVCurve_Voltage107 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 107
5157 | 1425 | IVCurve_Current107 | U16 | 0.01 | A |  |  | R | IV curve scan current 107
5158 | 1426 | IVCurve_Voltage108 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 108
5159 | 1427 | IVCurve_Current108 | U16 | 0.01 | A |  |  | R | IV curve sweep current 108
5160 | 1428 | IVCurve_Voltage109 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 109
5161 | 1429 | IVCurve_Current109 | U16 | 0.01 | A |  |  | R | IV curve scan current 109
5162 | 142A | IVCurve_Voltage110 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 110
5163 | 142B | IVCurve_Current110 | U16 | 0.01 | A |  |  | R | IV curve scan current 110
5164 | 142C | IVCurve_Voltage111 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 111
5165 | 142D | IVCurve_Current111 | U16 | 0.01 | A |  |  | R | IV curve scan current 111
5166 | 142E | IVCurve_Voltage112 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 112
5167 | 142F | IVCurve_Current112 | U16 | 0.01 | A |  |  | R | IV curve scan current 112
5168 | 1430 | IVCurve_Voltage113 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 113
5169 | 1431 | IVCurve_Current113 | U16 | 0.01 | A |  |  | R | IV curve scan current 113
5170 | 1432 | IVCurve_Voltage114 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 114
5171 | 1433 | IVCurve_Current114 | U16 | 0.01 | A |  |  | R | IV curve sweep current 114
5172 | 1434 | IVCurve_Voltage115 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 115
5173 | 1435 | IVCurve_Current115 | U16 | 0.01 | A |  |  | R | IV curve sweep current 115
5174 | 1436 | IVCurve_Voltage116 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 116
5175 | 1437 | IVCurve_Current116 | U16 | 0.01 | A |  |  | R | IV curve scan current 116
5176 | 1438 | IVCurve_Voltage117 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 117
5177 | 1439 | IVCurve_Current117 | U16 | 0.01 | A |  |  | R | IV curve scan current 117
5178 | 143A | IVCurve_Voltage118 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 118
5179 | 143B | IVCurve_Current118 | U16 | 0.01 | A |  |  | R | IV curve scan current 118
5180 | 143C | IVCurve_Voltage119 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 119
5181 | 143D | IVCurve_Current119 | U16 | 0.01 | A |  |  | R | IV curve scan current 119
5182 | 143E | IVCurve_Voltage120 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 120
5183 | 143F | IVCurve_Current120 | U16 | 0.01 | A |  |  | R | IV curve sweep current 120
5184 | 1440 | AddressMask_Config_ReadOnly_Result6 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid.
5185 | 1441
5186 | 1442
5187 | 1443
5188 | 1444 | IVCurve_Voltage121 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 121
5189 | 1445 | IVCurve_Current121 | U16 | 0.01 | A |  |  | R | IV curve scan current 121
5190 | 1446 | IVCurve_Voltage122 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 122
5191 | 1447 | IVCurve_Current122 | U16 | 0.01 | A |  |  | R | IV curve scan current 122
5192 | 1448 | IVCurve_Voltage123 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 123
5193 | 1449 | IVCurve_Current123 | U16 | 0.01 | A |  |  | R | IV curve scan current 123
5194 | 144A | IVCurve_Voltage124 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 124
5195 | 144B | IVCurve_Current124 | U16 | 0.01 | A |  |  | R | IV curve scan current 124
5196 | 144C | IVCurve_Voltage125 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 125
5197 | 144D | IVCurve_Current125 | U16 | 0.01 | A |  |  | R | IV curve sweep current 125
5198 | 144E | IVCurve_Voltage126 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 126
5199 | 144F | IVCurve_Current126 | U16 | 0.01 | A |  |  | R | IV curve scan current 126
5200 | 1450 | IVCurve_Voltage127 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 127
5201 | 1451 | IVCurve_Current127 | U16 | 0.01 | A |  |  | R | IV curve scan current 127
5202 | 1452 | IVCurve_Voltage128 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 128
5203 | 1453 | IVCurve_Current128 | U16 | 0.01 | A |  |  | R | IV curve scan current 128
5204 | 1454 | IVCurve_Voltage129 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 129
5205 | 1455 | IVCurve_Current129 | U16 | 0.01 | A |  |  | R | IV curve scan current 129
5206 | 1456 | IVCurve_Voltage130 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 130
5207 | 1457 | IVCurve_Current130 | U16 | 0.01 | A |  |  | R | IV curve scan current 130
5208 | 1458 | IVCurve_Voltage131 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 131
5209 | 1459 | IVCurve_Current131 | U16 | 0.01 | A |  |  | R | IV curve scan current 131
5210 | 145A | IVCurve_Voltage132 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 132
5211 | 145B | IVCurve_Current132 | U16 | 0.01 | A |  |  | R | IV curve scan current 132
5212 | 145C | IVCurve_Voltage133 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 133
5213 | 145D | IVCurve_Current133 | U16 | 0.01 | A |  |  | R | IV curve scan current 133
5214 | 145E | IVCurve_Voltage134 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 134
5215 | 145F | IVCurve_Current134 | U16 | 0.01 | A |  |  | R | IV curve scan current 134
5216 | 1460 | IVCurve_Voltage135 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 135
5217 | 1461 | IVCurve_Current135 | U16 | 0.01 | A |  |  | R | IV curve scan current 135
5218 | 1462 | IVCurve_Voltage136 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 136
5219 | 1463 | IVCurve_Current136 | U16 | 0.01 | A |  |  | R | IV curve scan current 136
5220 | 1464 | IVCurve_Voltage137 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 137
5221 | 1465 | IVCurve_Current137 | U16 | 0.01 | A |  |  | R | IV curve scan current 137
5222 | 1466 | IVCurve_Voltage138 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 138
5223 | 1467 | IVCurve_Current138 | U16 | 0.01 | A |  |  | R | IV curve scan current 138
5224 | 1468 | IVCurve_Voltage139 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 139
5225 | 1469 | IVCurve_Current139 | U16 | 0.01 | A |  |  | R | IV curve scan current 139
5226 | 146A | IVCurve_Voltage140 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 140
5227 | 146B | IVCurve_Current140 | U16 | 0.01 | A |  |  | R | IV curve sweep current 140
5228 | 146C | IVCurve_Voltage141 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 141
5229 | 146D | IVCurve_Current141 | U16 | 0.01 | A |  |  | R | IV curve scan current 141
5230 | 146E | IVCurve_Voltage142 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 142
5231 | 146F | IVCurve_Current142 | U16 | 0.01 | A |  |  | R | IV curve scan current 142
5232 | 1470 | IVCurve_Voltage143 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 143
5233 | 1471 | IVCurve_Current143 | U16 | 0.01 | A |  |  | R | IV curve scan current 143
5234 | 1472 | IVCurve_Voltage144 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 144
5235 | 1473 | IVCurve_Current144 | U16 | 0.01 | A |  |  | R | IV curve scan current 144
5236 | 1474 | IVCurve_Voltage145 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 145
5237 | 1475 | IVCurve_Current145 | U16 | 0.01 | A |  |  | R | IV curve scan current 145
5238 | 1476 | IVCurve_Voltage146 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 146
5239 | 1477 | IVCurve_Current146 | U16 | 0.01 | A |  |  | R | IV curve scan current 146
5240 | 1478 | IVCurve_Voltage147 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 147
5241 | 1479 | IVCurve_Current147 | U16 | 0.01 | A |  |  | R | IV curve scan current 147
5242 | 147A | IVCurve_Voltage148 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 148
5243 | 147B | IVCurve_Current148 | U16 | 0.01 | A |  |  | R | IV curve scan current 148
5244 | 147C | IVCurve_Voltage149 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 149
5245 | 147D | IVCurve_Current149 | U16 | 0.01 | A |  |  | R | IV curve scan current 149
5246 | 147E | IVCurve_Voltage150 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 150
5247 | 147F | IVCurve_Current150 | U16 | 0.01 | A |  |  | R | IV curve scan current 150
5248 | 1480 | HistoryEventList_ID1 | U16 |  |  |  |  | R | The latest 1st item of historical event ID
5249 | 1481 | HistoryEventList_yM1 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5250 | 1482 | HistoryEventList_dH1 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5251 | 1483 | HistoryEventList_ms1 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5252 | 1484 | HistoryEventList_ID2 | U16 |  |  |  |  | R | The 2nd most recent historical event ID
5253 | 1485 | HistoryEventList_yM2 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5254 | 1486 | HistoryEventList_dH2 | U16 |  |  |  |  | R | High byte: date; Low byte: hour. "
5255 | 1487 | HistoryEventList_ms2 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5256 | 1488 | HistoryEventList_ID3 | U16 |  |  |  |  | R | The 3rd most recent historical event ID
5257 | 1489 | HistoryEventList_yM3 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5258 | 148A | HistoryEventList_dH3 | U16 |  |  |  |  | R | High byte: date; Low byte: hour. "
5259 | 148B | HistoryEventList_ms3 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5260 | 148C | HistoryEventList_ID4 | U16 |  |  |  |  | R | The 4th most recent historical event ID
5261 | 148D | HistoryEventList_yM4 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5262 | 148E | HistoryEventList_dH4 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5263 | 148F | HistoryEventList_ms4 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5264 | 1490 | HistoryEventList_ID5 | U16 |  |  |  |  | R | The 5th most recent historical event ID
5265 | 1491 | HistoryEventList_yM5 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5266 | 1492 | HistoryEventList_dH5 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5267 | 1493 | HistoryEventList_ms5 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5268 | 1494 | HistoryEventList_ID6 | U16 |  |  |  |  | R | The 6th most recent historical event ID
5269 | 1495 | HistoryEventList_yM6 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5270 | 1496 | HistoryEventList_dH6 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5271 | 1497 | HistoryEventList_ms6 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5272 | 1498 | HistoryEventList_ID7 | U16 |  |  |  |  | R | The 7th most recent historical event ID
5273 | 1499 | HistoryEventList_yM7 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5274 | 149A | HistoryEventList_dH7 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5275 | 149B | HistoryEventList_ms7 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5276 | 149C | HistoryEventList_ID8 | U16 |  |  |  |  | R | The 8th most recent historical event ID
5277 | 149D | HistoryEventList_yM8 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5278 | 149E | HistoryEventList_dH8 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5279 | 149F | HistoryEventList_ms8 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5280 | 14A0 | HistoryEventList_ID9 | U16 |  |  |  |  | R | The 9th most recent historical event ID
5281 | 14A1 | HistoryEventList_yM9 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5282 | 14A2 | HistoryEventList_dH9 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5283 | 14A3 | HistoryEventList_ms9 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5284 | 14A4 | HistoryEventList_ID10 | U16 |  |  |  |  | R | The 10th most recent historical event ID
5285 | 14A5 | HistoryEventList_yM10 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5286 | 14A6 | HistoryEventList_dH10 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5287 | 14A7 | HistoryEventList_ms10 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5288 | 14A8 | HistoryEventList_ID11 | U16 |  |  |  |  | R | The 11th most recent historical event ID
5289 | 14A9 | HistoryEventList_yM11 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5290 | 14AA | HistoryEventList_dH11 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5291 | 14AB | HistoryEventList_ms11 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5292 | 14AC | HistoryEventList_ID12 | U16 |  |  |  |  | R | The 12th most recent historical event ID
5293 | 14AD | HistoryEventList_yM12 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5294 | 14AE | HistoryEventList_dH12 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5295 | 14AF | HistoryEventList_ms12 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5296 | 14B0 | HistoryEventList_ID13 | U16 |  |  |  |  | R | The 13th most recent historical event ID
5297 | 14B1 | HistoryEventList_yM13 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5298 | 14B2 | HistoryEventList_dH13 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5299 | 14B3 | HistoryEventList_ms13 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5300 | 14B4 | HistoryEventList_ID14 | U16 |  |  |  |  | R | The 14th most recent historical event ID
5301 | 14B5 | HistoryEventList_yM14 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5302 | 14B6 | HistoryEventList_dH14 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5303 | 14B7 | HistoryEventList_ms14 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5304 | 14B8 | HistoryEventList_ID15 | U16 |  |  |  |  | R | The 15th most recent historical event ID
5305 | 14B9 | HistoryEventList_yM15 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5306 | 14BA | HistoryEventList_dH15 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5307 | 14BB | HistoryEventList_ms15 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5308 | 14BC | HistoryEventList_ID16 | U16 |  |  |  |  | R | The 16th most recent historical event ID
5309 | 14BD | HistoryEventList_yM16 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5310 | 14BE | HistoryEventList_dH16 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5311 | 14BF | HistoryEventList_ms16 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5312 | 14C0 | HistoryEventList_ID17 | U16 |  |  |  |  | R | The 17th most recent historical event ID
5313 | 14C1 | HistoryEventList_yM17 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5314 | 14C2 | HistoryEventList_dH17 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5315 | 14C3 | HistoryEventList_ms17 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5316 | 14C4 | HistoryEventList_ID18 | U16 |  |  |  |  | R | The 18th most recent historical event ID
5317 | 14C5 | HistoryEventList_yM18 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5318 | 14C6 | HistoryEventList_dH18 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5319 | 14C7 | HistoryEventList_ms18 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5320 | 14C8 | HistoryEventList_ID19 | U16 |  |  |  |  | R | The 19th most recent historical event ID
5321 | 14C9 | HistoryEventList_yM19 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5322 | 14CA | HistoryEventList_dH19 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5323 | 14CB | HistoryEventList_ms19 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5324 | 14CC | HistoryEventList_ID20 | U16 |  |  |  |  | R | The 20th most recent historical event ID
5325 | 14CD | HistoryEventList_yM20 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5326 | 14CE | HistoryEventList_dH20 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5327 | 14CF | HistoryEventList_ms20 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5328 | 14D0 | HistoryEventList_ID21 | U16 |  |  |  |  | R | The 21th most recent historical event ID
5329 | 14D1 | HistoryEventList_yM21 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5330 | 14D2 | HistoryEventList_dH21 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5331 | 14D3 | HistoryEventList_ms21 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5332 | 14D4 | HistoryEventList_ID22 | U16 |  |  |  |  | R | The 22th most recent historical event ID
5333 | 14D5 | HistoryEventList_yM22 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5334 | 14D6 | HistoryEventList_dH22 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5335 | 14D7 | HistoryEventList_ms22 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5336 | 14D8 | HistoryEventList_ID23 | U16 |  |  |  |  | R | The 23th most recent historical event ID
5337 | 14D9 | HistoryEventList_yM23 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5338 | 14DA | HistoryEventList_dH23 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5339 | 14DB | HistoryEventList_ms23 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5340 | 14DC | HistoryEventList_ID24 | U16 |  |  |  |  | R | The 24th most recent historical event ID
5341 | 14DD | HistoryEventList_yM24 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5342 | 14DE | HistoryEventList_dH24 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5343 | 14DF | HistoryEventList_ms24 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5344 | 14E0 | HistoryEventList_ID25 | U16 |  |  |  |  | R | The 25th most recent historical event ID
5345 | 14E1 | HistoryEventList_yM25 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5346 | 14E2 | HistoryEventList_dH25 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5347 | 14E3 | HistoryEventList_ms25 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5348 | 14E4 | HistoryEventList_ID26 | U16 |  |  |  |  | R | The 26th most recent historical event ID
5349 | 14E5 | HistoryEventList_yM26 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5350 | 14E6 | HistoryEventList_dH26 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5351 | 14E7 | HistoryEventList_ms26 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5352 | 14E8 | HistoryEventList_ID27 | U16 |  |  |  |  | R | The 27th most recent historical event ID
5353 | 14E9 | HistoryEventList_yM27 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5354 | 14EA | HistoryEventList_dH27 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5355 | 14EB | HistoryEventList_ms27 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5356 | 14EC | HistoryEventList_ID28 | U16 |  |  |  |  | R | The 28th most recent historical event ID
5357 | 14ED | HistoryEventList_yM28 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5358 | 14EE | HistoryEventList_dH28 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5359 | 14EF | HistoryEventList_ms28 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5360 | 14F0 | HistoryEventList_ID29 | U16 |  |  |  |  | R | The 29th most recent historical event ID
5361 | 14F1 | HistoryEventList_yM29 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5362 | 14F2 | HistoryEventList_dH29 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5363 | 14F3 | HistoryEventList_ms29 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5364 | 14F4 | HistoryEventList_ID30 | U16 |  |  |  |  | R | The 30th most recent historical event ID
5365 | 14F5 | HistoryEventList_yM30 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5366 | 14F6 | HistoryEventList_dH30 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5367 | 14F7 | HistoryEventList_ms30 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5368 | 14F8 | HistoryEventList_ID31 | U16 |  |  |  |  | R | The 31th most recent historical event ID
5369 | 14F9 | HistoryEventList_yM31 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5370 | 14FA | HistoryEventList_dH31 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5371 | 14FB | HistoryEventList_ms31 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5372 | 14FC | HistoryEventList_ID32 | U16 |  |  |  |  | R | The 32th most recent historical event ID
5373 | 14FD | HistoryEventList_yM32 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5374 | 14FE | HistoryEventList_dH32 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5375 | 14FF | HistoryEventList_ms32 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5376 | 1500 | HistoryEventList_ID33 | U16 |  |  |  |  | R | The 33th most recent historical event ID
5377 | 1501 | HistoryEventList_yM33 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5378 | 1502 | HistoryEventList_dH33 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5379 | 1503 | HistoryEventList_ms33 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5380 | 1504 | HistoryEventList_ID34 | U16 |  |  |  |  | R | The 34th most recent historical event ID
5381 | 1505 | HistoryEventList_yM34 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5382 | 1506 | HistoryEventList_dH34 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5383 | 1507 | HistoryEventList_ms34 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5384 | 1508 | HistoryEventList_ID35 | U16 |  |  |  |  | R | The 35th most recent historical event ID
5385 | 1509 | HistoryEventList_yM35 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5386 | 150A | HistoryEventList_dH35 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5387 | 150B | HistoryEventList_ms35 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5388 | 150C | HistoryEventList_ID36 | U16 |  |  |  |  | R | The 36th most recent historical event ID
5389 | 150D | HistoryEventList_yM36 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5390 | 150E | HistoryEventList_dH36 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5391 | 150F | HistoryEventList_ms36 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5392 | 1510 | HistoryEventList_ID37 | U16 |  |  |  |  | R | The 37th most recent historical event ID
5393 | 1511 | HistoryEventList_yM37 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5394 | 1512 | HistoryEventList_dH37 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5395 | 1513 | HistoryEventList_ms37 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5396 | 1514 | HistoryEventList_ID38 | U16 |  |  |  |  | R | The 38th most recent historical event ID
5397 | 1515 | HistoryEventList_yM38 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5398 | 1516 | HistoryEventList_dH38 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5399 | 1517 | HistoryEventList_ms38 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5400 | 1518 | HistoryEventList_ID39 | U16 |  |  |  |  | R | The 39th most recent historical event ID
5401 | 1519 | HistoryEventList_yM39 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5402 | 151A | HistoryEventList_dH39 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5403 | 151B | HistoryEventList_ms39 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5404 | 151C | HistoryEventList_ID40 | U16 |  |  |  |  | R | The 40th most recent historical event ID
5405 | 151D | HistoryEventList_yM40 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5406 | 151E | HistoryEventList_dH40 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5407 | 151F | HistoryEventList_ms40 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5408 | 1520 | HistoryEventList_ID41 | U16 |  |  |  |  | R | The 41th most recent historical event ID
5409 | 1521 | HistoryEventList_yM41 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5410 | 1522 | HistoryEventList_dH41 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5411 | 1523 | HistoryEventList_ms41 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5412 | 1524 | HistoryEventList_ID42 | U16 |  |  |  |  | R | The 42th most recent historical event ID
5413 | 1525 | HistoryEventList_yM42 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5414 | 1526 | HistoryEventList_dH42 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5415 | 1527 | HistoryEventList_ms42 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5416 | 1528 | HistoryEventList_ID43 | U16 |  |  |  |  | R | The 43th most recent historical event ID
5417 | 1529 | HistoryEventList_yM43 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5418 | 152A | HistoryEventList_dH43 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5419 | 152B | HistoryEventList_ms43 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5420 | 152C | HistoryEventList_ID44 | U16 |  |  |  |  | R | The 44th most recent historical event ID
5421 | 152D | HistoryEventList_yM44 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5422 | 152E | HistoryEventList_dH44 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5423 | 152F | HistoryEventList_ms44 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5424 | 1530 | HistoryEventList_ID45 | U16 |  |  |  |  | R | The 45th most recent historical event ID
5425 | 1531 | HistoryEventList_yM45 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5426 | 1532 | HistoryEventList_dH45 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5427 | 1533 | HistoryEventList_ms45 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5428 | 1534 | HistoryEventList_ID46 | U16 |  |  |  |  | R | The 46th most recent historical event ID
5429 | 1535 | HistoryEventList_yM46 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5430 | 1536 | HistoryEventList_dH46 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5431 | 1537 | HistoryEventList_ms46 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5432 | 1538 | HistoryEventList_ID47 | U16 |  |  |  |  | R | The 47th most recent historical event ID
5433 | 1539 | HistoryEventList_yM47 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5434 | 153A | HistoryEventList_dH47 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5435 | 153B | HistoryEventList_ms47 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5436 | 153C | HistoryEventList_ID48 | U16 |  |  |  |  | R | The 48th most recent historical event ID
5437 | 153D | HistoryEventList_yM48 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5438 | 153E | HistoryEventList_dH48 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5439 | 153F | HistoryEventList_ms48 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5440 | 1540 | HistoryEventList_ID49 | U16 |  |  |  |  | R | The 49th most recent historical event ID
5441 | 1541 | HistoryEventList_yM49 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5442 | 1542 | HistoryEventList_dH49 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5443 | 1543 | HistoryEventList_ms49 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5444 | 1544 | HistoryEventList_ID50 | U16 |  |  |  |  | R | The 50th most recent historical event ID
5445 | 1545 | HistoryEventList_yM50 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5446 | 1546 | HistoryEventList_dH50 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5447 | 1547 | HistoryEventList_ms50 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5448 | 1548 | HistoryEventList_ID51 | U16 |  |  |  |  | R | The 51th most recent historical event ID
5449 | 1549 | HistoryEventList_yM51 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5450 | 154A | HistoryEventList_dH51 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5451 | 154B | HistoryEventList_ms51 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5452 | 154C | HistoryEventList_ID52 | U16 |  |  |  |  | R | The 52th most recent historical event ID
5453 | 154D | HistoryEventList_yM52 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5454 | 154E | HistoryEventList_dH52 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5455 | 154F | HistoryEventList_ms52 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5456 | 1550 | HistoryEventList_ID53 | U16 |  |  |  |  | R | The 53th most recent historical event ID
5457 | 1551 | HistoryEventList_yM53 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5458 | 1552 | HistoryEventList_dH53 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5459 | 1553 | HistoryEventList_ms53 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5460 | 1554 | HistoryEventList_ID54 | U16 |  |  |  |  | R | The 54th most recent historical event ID
5461 | 1555 | HistoryEventList_yM54 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5462 | 1556 | HistoryEventList_dH54 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5463 | 1557 | HistoryEventList_ms54 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5464 | 1558 | HistoryEventList_ID55 | U16 |  |  |  |  | R | The 55th most recent historical event ID
5465 | 1559 | HistoryEventList_yM55 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5466 | 155A | HistoryEventList_dH55 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5467 | 155B | HistoryEventList_ms55 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5468 | 155C | HistoryEventList_ID56 | U16 |  |  |  |  | R | The 56th most recent historical event ID
5469 | 155D | HistoryEventList_yM56 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5470 | 155E | HistoryEventList_dH56 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5471 | 155F | HistoryEventList_ms56 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5472 | 1560 | HistoryEventList_ID57 | U16 |  |  |  |  | R | The 57th most recent historical event ID
5473 | 1561 | HistoryEventList_yM57 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5474 | 1562 | HistoryEventList_dH57 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5475 | 1563 | HistoryEventList_ms57 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5476 | 1564 | HistoryEventList_ID58 | U16 |  |  |  |  | R | The 58th most recent historical event ID
5477 | 1565 | HistoryEventList_yM58 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5478 | 1566 | HistoryEventList_dH58 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5479 | 1567 | HistoryEventList_ms58 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5480 | 1568 | HistoryEventList_ID59 | U16 |  |  |  |  | R | The 59th most recent historical event ID
5481 | 1569 | HistoryEventList_yM59 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5482 | 156A | HistoryEventList_dH59 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5483 | 156B | HistoryEventList_ms59 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5484 | 156C | HistoryEventList_ID60 | U16 |  |  |  |  | R | The 60th most recent historical event ID
5485 | 156D | HistoryEventList_yM60 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5486 | 156E | HistoryEventList_dH60 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5487 | 156F | HistoryEventList_ms60 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5488 | 1570 | HistoryEventList_ID61 | U16 |  |  |  |  | R | The 61th most recent historical event ID
5489 | 1571 | HistoryEventList_yM61 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5490 | 1572 | HistoryEventList_dH61 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5491 | 1573 | HistoryEventList_ms61 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5492 | 1574 | HistoryEventList_ID62 | U16 |  |  |  |  | R | The 62th most recent historical event ID
5493 | 1575 | HistoryEventList_yM62 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5494 | 1576 | HistoryEventList_dH62 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5495 | 1577 | HistoryEventList_ms62 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5496 | 1578 | HistoryEventList_ID63 | U16 |  |  |  |  | R | The 63th most recent historical event ID
5497 | 1579 | HistoryEventList_yM63 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5498 | 157A | HistoryEventList_dH63 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5499 | 157B | HistoryEventList_ms63 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5500 | 157C | HistoryEventList_ID64 | U16 |  |  |  |  | R | The 64th most recent historical event ID
5501 | 157D | HistoryEventList_yM64 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5502 | 157E | HistoryEventList_dH64 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5503 | 157F | HistoryEventList_ms64 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5504 | 1580 | HistoryEventList_ID65 | U16 |  |  |  |  | R | The 65th most recent historical event ID
5505 | 1581 | HistoryEventList_yM65 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5506 | 1582 | HistoryEventList_dH65 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5507 | 1583 | HistoryEventList_ms65 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5508 | 1584 | HistoryEventList_ID66 | U16 |  |  |  |  | R | The 66th most recent historical event ID
5509 | 1585 | HistoryEventList_yM66 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5510 | 1586 | HistoryEventList_dH66 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5511 | 1587 | HistoryEventList_ms66 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5512 | 1588 | HistoryEventList_ID67 | U16 |  |  |  |  | R | The 67th most recent historical event ID
5513 | 1589 | HistoryEventList_yM67 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5514 | 158A | HistoryEventList_dH67 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5515 | 158B | HistoryEventList_ms67 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5516 | 158C | HistoryEventList_ID68 | U16 |  |  |  |  | R | The 68th most recent historical event ID
5517 | 158D | HistoryEventList_yM68 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5518 | 158E | HistoryEventList_dH68 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5519 | 158F | HistoryEventList_ms68 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5520 | 1590 | HistoryEventList_ID69 | U16 |  |  |  |  | R | The 69th most recent historical event ID
5521 | 1591 | HistoryEventList_yM69 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5522 | 1592 | HistoryEventList_dH69 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5523 | 1593 | HistoryEventList_ms69 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5524 | 1594 | HistoryEventList_ID70 | U16 |  |  |  |  | R | The 70th most recent historical event ID
5525 | 1595 | HistoryEventList_yM70 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5526 | 1596 | HistoryEventList_dH70 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5527 | 1597 | HistoryEventList_ms70 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5528 | 1598 | HistoryEventList_ID71 | U16 |  |  |  |  | R | The 71th most recent historical event ID
5529 | 1599 | HistoryEventList_yM71 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5530 | 159A | HistoryEventList_dH71 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5531 | 159B | HistoryEventList_ms71 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5532 | 159C | HistoryEventList_ID72 | U16 |  |  |  |  | R | The 72th most recent historical event ID
5533 | 159D | HistoryEventList_yM72 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5534 | 159E | HistoryEventList_dH72 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5535 | 159F | HistoryEventList_ms72 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5536 | 15A0 | HistoryEventList_ID73 | U16 |  |  |  |  | R | The 73th most recent historical event ID
5537 | 15A1 | HistoryEventList_yM73 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5538 | 15A2 | HistoryEventList_dH73 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5539 | 15A3 | HistoryEventList_ms73 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5540 | 15A4 | HistoryEventList_ID74 | U16 |  |  |  |  | R | The 74th most recent historical event ID
5541 | 15A5 | HistoryEventList_yM74 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5542 | 15A6 | HistoryEventList_dH74 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5543 | 15A7 | HistoryEventList_ms74 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5544 | 15A8 | HistoryEventList_ID75 | U16 |  |  |  |  | R | The 75th most recent historical event ID
5545 | 15A9 | HistoryEventList_yM75 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5546 | 15AA | HistoryEventList_dH75 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5547 | 15AB | HistoryEventList_ms75 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5548 | 15AC | HistoryEventList_ID76 | U16 |  |  |  |  | R | The 76th most recent historical event ID
5549 | 15AD | HistoryEventList_yM76 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5550 | 15AE | HistoryEventList_dH76 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5551 | 15AF | HistoryEventList_ms76 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5552 | 15B0 | HistoryEventList_ID77 | U16 |  |  |  |  | R | The 77th most recent historical event ID
5553 | 15B1 | HistoryEventList_yM77 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5554 | 15B2 | HistoryEventList_dH77 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5555 | 15B3 | HistoryEventList_ms77 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5556 | 15B4 | HistoryEventList_ID78 | U16 |  |  |  |  | R | The 78th most recent historical event ID
5557 | 15B5 | HistoryEventList_yM78 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5558 | 15B6 | HistoryEventList_dH78 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5559 | 15B7 | HistoryEventList_ms78 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5560 | 15B8 | HistoryEventList_ID79 | U16 |  |  |  |  | R | The 79th most recent historical event ID
5561 | 15B9 | HistoryEventList_yM79 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5562 | 15BA | HistoryEventList_dH79 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5563 | 15BB | HistoryEventList_ms79 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5564 | 15BC | HistoryEventList_ID80 | U16 |  |  |  |  | R | The 80th most recent historical event ID
5565 | 15BD | HistoryEventList_yM80 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5566 | 15BE | HistoryEventList_dH80 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5567 | 15BF | HistoryEventList_ms80 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5568 | 15C0 | HistoryEventList_ID81 | U16 |  |  |  |  | R | The 81th most recent historical event ID
5569 | 15C1 | HistoryEventList_yM81 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5570 | 15C2 | HistoryEventList_dH81 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5571 | 15C3 | HistoryEventList_ms81 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5572 | 15C4 | HistoryEventList_ID82 | U16 |  |  |  |  | R | The 82th most recent historical event ID
5573 | 15C5 | HistoryEventList_yM82 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5574 | 15C6 | HistoryEventList_dH82 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5575 | 15C7 | HistoryEventList_ms82 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5576 | 15C8 | HistoryEventList_ID83 | U16 |  |  |  |  | R | The 83th most recent historical event ID
5577 | 15C9 | HistoryEventList_yM83 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5578 | 15CA | HistoryEventList_dH83 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5579 | 15CB | HistoryEventList_ms83 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5580 | 15CC | HistoryEventList_ID84 | U16 |  |  |  |  | R | The 84th most recent historical event ID
5581 | 15CD | HistoryEventList_yM84 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5582 | 15CE | HistoryEventList_dH84 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5583 | 15CF | HistoryEventList_ms84 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5584 | 15D0 | HistoryEventList_ID85 | U16 |  |  |  |  | R | The 85th most recent historical event ID
5585 | 15D1 | HistoryEventList_yM85 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5586 | 15D2 | HistoryEventList_dH85 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5587 | 15D3 | HistoryEventList_ms85 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5588 | 15D4 | HistoryEventList_ID86 | U16 |  |  |  |  | R | The 86th most recent historical event ID
5589 | 15D5 | HistoryEventList_yM86 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5590 | 15D6 | HistoryEventList_dH86 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5591 | 15D7 | HistoryEventList_ms86 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5592 | 15D8 | HistoryEventList_ID87 | U16 |  |  |  |  | R | The 87th most recent historical event ID
5593 | 15D9 | HistoryEventList_yM87 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5594 | 15DA | HistoryEventList_dH87 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5595 | 15DB | HistoryEventList_ms87 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5596 | 15DC | HistoryEventList_ID88 | U16 |  |  |  |  | R | The 88th most recent historical event ID
5597 | 15DD | HistoryEventList_yM88 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5598 | 15DE | HistoryEventList_dH88 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5599 | 15DF | HistoryEventList_ms88 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5600 | 15E0 | HistoryEventList_ID89 | U16 |  |  |  |  | R | The 89th most recent historical event ID
5601 | 15E1 | HistoryEventList_yM89 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5602 | 15E2 | HistoryEventList_dH89 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5603 | 15E3 | HistoryEventList_ms89 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5604 | 15E4 | HistoryEventList_ID90 | U16 |  |  |  |  | R | The 90th most recent historical event ID
5605 | 15E5 | HistoryEventList_yM90 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5606 | 15E6 | HistoryEventList_dH90 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5607 | 15E7 | HistoryEventList_ms90 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5608 | 15E8 | HistoryEventList_ID91 | U16 |  |  |  |  | R | The 91th most recent historical event ID
5609 | 15E9 | HistoryEventList_yM91 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5610 | 15EA | HistoryEventList_dH91 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5611 | 15EB | HistoryEventList_ms91 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5612 | 15EC | HistoryEventList_ID92 | U16 |  |  |  |  | R | The 92th most recent historical event ID
5613 | 15ED | HistoryEventList_yM92 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5614 | 15EE | HistoryEventList_dH92 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5615 | 15EF | HistoryEventList_ms92 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5616 | 15F0 | HistoryEventList_ID93 | U16 |  |  |  |  | R | The 93th most recent historical event ID
5617 | 15F1 | HistoryEventList_yM93 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5618 | 15F2 | HistoryEventList_dH93 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5619 | 15F3 | HistoryEventList_ms93 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5620 | 15F4 | HistoryEventList_ID94 | U16 |  |  |  |  | R | The 94th most recent historical event ID
5621 | 15F5 | HistoryEventList_yM94 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5622 | 15F6 | HistoryEventList_dH94 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5623 | 15F7 | HistoryEventList_ms94 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5624 | 15F8 | HistoryEventList_ID95 | U16 |  |  |  |  | R | The 95th most recent historical event ID
5625 | 15F9 | HistoryEventList_yM95 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5626 | 15FA | HistoryEventList_dH95 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5627 | 15FB | HistoryEventList_ms95 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5628 | 15FC | HistoryEventList_ID96 | U16 |  |  |  |  | R | The 96th most recent historical event ID
5629 | 15FD | HistoryEventList_yM96 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5630 | 15FE | HistoryEventList_dH96 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5631 | 15FF | HistoryEventList_ms96 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5632 | 1600 | HistoryEventList_ID97 | U16 |  |  |  |  | R | The 97th most recent historical event ID
5633 | 1601 | HistoryEventList_yM97 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5634 | 1602 | HistoryEventList_dH97 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5635 | 1603 | HistoryEventList_ms97 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5636 | 1604 | HistoryEventList_ID98 | U16 |  |  |  |  | R | The 98th most recent historical event ID
5637 | 1605 | HistoryEventList_yM98 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5638 | 1606 | HistoryEventList_dH98 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5639 | 1607 | HistoryEventList_ms98 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5640 | 1608 | HistoryEventList_ID99 | U16 |  |  |  |  | R | The 99th most recent historical event ID
5641 | 1609 | HistoryEventList_yM99 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5642 | 160A | HistoryEventList_dH99 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5643 | 160B | HistoryEventList_ms99 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5644 | 160C | HistoryEventList_ID100 | U16 |  |  |  |  | R | The 100th most recent historical event ID
5645 | 160D | HistoryEventList_yM100 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
5646 | 160E | HistoryEventList_dH100 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
5647 | 160F | HistoryEventList_ms100 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
5648 | 1610 | EnergyStatistics1 | U32 | 0.01 | kWh |  |  | R | Article 1 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5649 | 1611
5650 | 1612 | EnergyStatistics2 | U32 | 0.01 | kWh |  |  | R | Article 2 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5651 | 1613
5652 | 1614 | EnergyStatistics3 | U32 | 0.01 | kWh |  |  | R | Article 3 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5653 | 1615
5654 | 1616 | EnergyStatistics4 | U32 | 0.01 | kWh |  |  | R | Article 4 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5655 | 1617
5656 | 1618 | EnergyStatistics5 | U32 | 0.01 | kWh |  |  | R | Article 5 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5657 | 1619
5658 | 161A | EnergyStatistics6 | U32 | 0.01 | kWh |  |  | R | Article 6 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5659 | 161B
5660 | 161C | EnergyStatistics7 | U32 | 0.01 | kWh |  |  | R | Article 7 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5661 | 161D
5662 | 161E | EnergyStatistics8 | U32 | 0.01 | kWh |  |  | R | Article 8 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5663 | 161F
5664 | 1620 | EnergyStatistics9 | U32 | 0.01 | kWh |  |  | R | Article 9 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5665 | 1621
5666 | 1622 | EnergyStatistics10 | U32 | 0.01 | kWh |  |  | R | Article 10 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5667 | 1623
5668 | 1624 | EnergyStatistics11 | U32 | 0.01 | kWh |  |  | R | Article 11 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5669 | 1625
5670 | 1626 | EnergyStatistics12 | U32 | 0.01 | kWh |  |  | R | Article 12 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5671 | 1627
5672 | 1628 | EnergyStatistics13 | U32 | 0.01 | kWh |  |  | R | Article 13 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5673 | 1629
5674 | 162A | EnergyStatistics14 | U32 | 0.01 | kWh |  |  | R | Article 14 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5675 | 162B
5676 | 162C | EnergyStatistics15 | U32 | 0.01 | kWh |  |  | R | Article 15 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5677 | 162D
5678 | 162E | EnergyStatistics16 | U32 | 0.01 | kWh |  |  | R | Article 16 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5679 | 162F
5680 | 1630 | EnergyStatistics17 | U32 | 0.01 | kWh |  |  | R | Article 17 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5681 | 1631
5682 | 1632 | EnergyStatistics18 | U32 | 0.01 | kWh |  |  | R | Article 18 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5683 | 1633
5684 | 1634 | EnergyStatistics19 | U32 | 0.01 | kWh |  |  | R | Article 19 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5685 | 1635
5686 | 1636 | EnergyStatistics20 | U32 | 0.01 | kWh |  |  | R | Article 20 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5687 | 1637
5688 | 1638 | EnergyStatistics21 | U32 | 0.01 | kWh |  |  | R | Article 21 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5689 | 1639
5690 | 163A | EnergyStatistics22 | U32 | 0.01 | kWh |  |  | R | Article 22 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5691 | 163B
5692 | 163C | EnergyStatistics23 | U32 | 0.01 | kWh |  |  | R | Article 23 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5693 | 163D
5694 | 163E | EnergyStatistics24 | U32 | 0.01 | kWh |  |  | R | Article 24 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5695 | 163F
5696 | 1640 | EnergyStatistics25 | U32 | 0.01 | kWh |  |  | R | Article 25 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5697 | 1641
5698 | 1642 | EnergyStatistics26 | U32 | 0.01 | kWh |  |  | R | Article 26 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5699 | 1643
5700 | 1644 | EnergyStatistics27 | U32 | 0.01 | kWh |  |  | R | Article 27 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5701 | 1645
5702 | 1646 | EnergyStatistics28 | U32 | 0.01 | kWh |  |  | R | Article 28 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5703 | 1647
5704 | 1648 | EnergyStatistics29 | U32 | 0.01 | kWh |  |  | R | Article 29 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5705 | 1649
5706 | 164A | EnergyStatistics30 | U32 | 0.01 | kWh |  |  | R | Article 30 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5707 | 164B
5708 | 164C | EnergyStatistics31 | U32 | 0.01 | kWh |  |  | R | Article 31 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5709 | 164D
5710 | 164E | EnergyStatistics32 | U32 | 0.01 | kWh |  |  | R | Article 32 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5711 | 164F
5712 | 1650 | EnergyStatistics33 | U32 | 0.01 | kWh |  |  | R | Article 33 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5713 | 1651
5714 | 1652 | EnergyStatistics34 | U32 | 0.01 | kWh |  |  | R | Article 34 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5715 | 1653
5716 | 1654 | EnergyStatistics35 | U32 | 0.01 | kWh |  |  | R | Article 35 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5717 | 1655
5718 | 1656 | EnergyStatistics36 | U32 | 0.01 | kWh |  |  | R | Article 36 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5719 | 1657
5720 | 1658 | EnergyStatistics37 | U32 | 0.01 | kWh |  |  | R | Article 37 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5721 | 1659
5722 | 165A | EnergyStatistics38 | U32 | 0.01 | kWh |  |  | R | Article 38 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5723 | 165B
5724 | 165C | EnergyStatistics39 | U32 | 0.01 | kWh |  |  | R | Article 39 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5725 | 165D
5726 | 165E | EnergyStatistics40 | U32 | 0.01 | kWh |  |  | R | Article 40 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
5727 | 165F
Core function configuration (0x2000-0x207F)
8192 | 2000 | AddressMask_Config_Core1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid.
8193 | 2001
8194 | 2002
8195 | 2003
8196 | 2004 | Country_Code | U16 |  |  |  |  | RW | Safety country, used for storage
8197 | 2005 | Safety_Version | U16 |  |  |  |  | RW | The version number of the safety parameters of the communication host (upper computer).
8198 | 2006 | Factory_Reset | U16 |  |  | 1 | 255 | RW | Restore factory registers; The bit value is 1 valid. Bit0: Clear battery Bit1: Clear event record Bit2: Restore default values ​​for all function configuration parameters When reading, return the status of the last write operation: 0x0000: success 0x0001-0x00FF: operating 0xFFFB: The operation failed and the controller refused to respond (maybe the controller is busy or the configuration is wrong) 0xFFFC: The operation failed and the controller did not respond 0xFFFD: Operation failed, current function is forbidden 0xFFFE: Operation failed, parameter access failed 0xFFFF: The operation failed, the input parameter is wrong
8199 | 2007 | Safety_Name1 | ASCII |  |  |  |  | RW | The first and second place in the name of the safety-regulated country. The upper 8 bits of the register store the first digit of the safety name; The lower 8 bits of the register store the second bit of the safety name.
8200 | 2008 | Safety_Name2 | ASCII |  |  |  |  | RW | The third and fourth place in the name of the safety-regulated country. The upper 8 bits of the register store the third digit of the safety name; The lower 8 bits of the register store the 4th bit of the safety name.
8201 | 2009 | Safety_Name3 | ASCII |  |  |  |  | RW | The 5th and 6th place in the name of the safety-regulated country. The upper 8 bits of the register store the 5th digit of the safety name; The lower 8 bits of the register store the 6th bit of the safety name.
8202 | 200A | Safety_Name4 | ASCII |  |  |  |  | RW | The 7th and 8th place in the name of the safety-regulated country. The upper 8 bits of the register store the 7th bit of the safety name; The lower 8 bits of the register store the 8th bit of the safety name.
8203 | 200B | Safety_Name5 | ASCII |  |  |  |  | RW | The ninth and tenth place in the name of safety regulations. The upper 8 bits of the register store the 9th bit of the safety name; The lower 8 bits of the register store the 10th bit of the safety name.
8204 | 200C
8205 | 200D
8206 | 200E
8207 | 200F
8208 | 2010
8209 | 2011
8210 | 2012
8211 | 2013
8212 | 2014
8213 | 2015
8214 | 2016
8215 | 2017
8216 | 2018
8217 | 2019
8218 | 201A
8219 | 201B
8220 | 201C
8221 | 201D
8222 | 201E
8223 | 201F
8224 | 2020
8225 | 2021
8226 | 2022
8227 | 2023
8228 | 2024
8229 | 2025
8230 | 2026
8231 | 2027
8232 | 2028
8233 | 2029
8234 | 202A
8235 | 202B
8236 | 202C
8237 | 202D
8238 | 202E
8239 | 202F
8240 | 2030
8241 | 2031
8242 | 2032
8243 | 2033
8244 | 2034
8245 | 2035
8246 | 2036
8247 | 2037
8248 | 2038
8249 | 2039
8250 | 203A
8251 | 203B
8252 | 203C
8253 | 203D | Remote_Upgrade_Control | U16 |  |  |  |  | W | Remote upgrade control register. High byte. Writing 0xA5 is valid. The low byte contains the chip combination that needs to be upgraded, and the explanation of each bit is as follows: Bit0: communication board; Bit1: control board 1 (main DSP); Bit2: control board 2 (secondary DSP); Bit3: Fuse
8254 | 203E | Local_Upgrade_Control | U16 |  |  |  |  | W | High byte. Writing 0xA5 is valid. The low byte contains the chip combination that needs to be upgraded, and the explanation of each bit is as follows: Bit0: communication board; Bit1: control board 1 (main DSP); Bit2: control board 2 (secondary DSP); Bit3: Fuse
8255 | 203F | Local_Upgrade_Status | U16 |  |  |  |  | R | Current upgrade progress The high byte indicates the current target chip to be upgraded: 0x00: Not in the upgrade state; 0x01: Main DSP upgrade; 0x02: Secondary DSP upgrade; 0x03: ARM upgrade; 0x04: FUSE upgrade; The low byte indicates the current upgrade progress: The progress range is 0-100%
ODM data customization area (0x7000-0x707F)
28672 | 7000 |  | ASCII |  |  |  |  | RW | The address of 0x7000-0x707F is a custom area, which must meet the following format: All registers in this area are in ASCII format. The upper 8 bits of the register store front-end characters and the lower 8 bits store back-end characters. For example, when the character string "1234" is stored in 0x7000, 0x7001, the data in 0x7000 is 0x3132; the data in 0x7001 is 0x3334. Allowed characters include: 0x20-0x7E and 0xFF. 0xFF is automatically ignored during parsing. The string format is defined as follows: Key 1=value 1\r\nkey 2=value 2\r\n The keys supported by this protocol version are: "SN": ODM serial number | End User
BMS（0x9000-0x9FFF）
36864 | 9000 | AddressMask_BMS1_System | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid.
36865 | 9001
36866 | 9002
36867 | 9003
36868 | 9004 | BMS_Sys_Time | U32 |  |  |  |  | R | BMS system clock Bit0-5: second, range 0-59 Bit6-11: minute, range 0-59 Bit12-16: hour, range 0-23 Bit17-21: day, range 1-31 Bit22-25: month, range 1-12 Bit26-31: year, range 0-63 (starting in 2000)
36869 | 9005
36870 | 9006 | BMS_CAN_Version | U16 |  |  |  |  | R | CAN protocol version number
36871 | 9007 | BMS_Manufacture_Name0 | U16 |  |  |  |  | R | Manufacturer Information 0
36872 | 9008 | BMS_Manufacture_Name1 | U16 |  |  |  |  | R | Manufacturer Information 1
36873 | 9009 | BMS_Manufacture_Name2 | U16 |  |  |  |  | R | Manufacturer Information 2
36874 | 900A | BMS_Manufacture_Name3 | U16 |  |  |  |  | R | Manufacturer Information 3
36875 | 900B | BMS_Version | U16 |  |  |  |  | R | BMS version number
36876 | 900C | Cell_Type | U16 |  |  |  |  | R | Cell type
36877 | 900D | BaPack_Number | U16 |  |  |  |  | R | High 8 bits: the number of battery packs in parallel Lower 8 bits: the number of battery strings in the battery pack
36878 | 900E | Realtime_Capacity | U16 | 1 | % |  |  | R | Real-time remaining capacity
36879 | 900F | Total_Voltage | U16 | 0.1 | V |  |  | R | Total voltage
36880 | 9010 | Total_Current | U16 | 0.1 | A |  |  | R | Total current
36881 | 9011 | Cell_Average_Temperature | U16 | 0.1 | ℃ |  |  | R | Average cell temperature
36882 | 9012 | SOC | U16 | 1 | % |  |  | R | State of charge
36883 | 9013 | SOH | U16 | 1 | % |  |  | R | Health
36884 | 9014 | BMS_Sys_Protect0 | U16 |  |  |  |  | R | BMS system protection information0
36885 | 9015 | BMS_Sys_Protect1 | U16 |  |  |  |  | R | BMS system protection information 1
36886 | 9016 | BMS_Sys_Alarm0 | U16 |  |  |  |  | R | BMS system alarm information 0
36887 | 9017 | BMS_Sys_Alarm1 | U16 |  |  |  |  | R | BMS system alarm information 1
36888 | 9018
36889 | 9019
36890 | 901A
36891 | 901B
36892 | 901C
36893 | 901D
36894 | 901E
36895 | 901F
36896 | 9020 | BMS_Inquire | U16 |  |  |  |  | RW | Battery query control word Bit0-7: The serial number of the battery pack to be queried, the valid range is 0~15, and 0 means the first battery pack Bit8-11: The serial number of the battery pack to be queried, the valid range is 0~15, and 0 means the first battery pack Bit12-15: The serial number of the fault to be queried, the valid range is 0~5, and 0 means the most recent fault
36897 | 9021
36898 | 9022
36899 | 9023
36900 | 9024
36901 | 9025
36902 | 9026
36903 | 9027
36904 | 9028
36905 | 9029
36906 | 902A
36907 | 902B
36908 | 902C
36909 | 902D
36910 | 902E
36911 | 902F
36912 | 9030
36913 | 9031
36914 | 9032
36915 | 9033
36916 | 9034
36917 | 9035
36918 | 9036
36919 | 9037
36920 | 9038
36921 | 9039
36922 | 903A
36923 | 903B
36924 | 903C
36925 | 903D
36926 | 903E
36927 | 903F
36928 | 9040 | AddressMask_BMS2_Realtime | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid.
36929 | 9041
36930 | 9042
36931 | 9043
36932 | 9044 | Pack_RT_ID | U16 |  |  |  |  | R | Real-time data battery pack number. High 8 bits: battery pack serial number Lower 8 bits: battery pack serial number"
36933 | 9045 | Pack_RT_Timestamp | U32 |  |  |  |  | R | Real-time data timestamp
36934 | 9046
36935 | 9047 | Pack_RT_SN0 | U16 |  |  |  |  | R | Device serial number 0
36936 | 9048 | Pack_RT_SN1 | U16 |  |  |  |  | R | Device serial number 1
36937 | 9049 | Pack_RT_SN2 | U16 |  |  |  |  | R | Device serial number 2
36938 | 904A | Pack_RT_SN3 | U16 |  |  |  |  | R | Device serial number 3
36939 | 904B | Pack_RT_SN4 | U16 |  |  |  |  | R | Device serial number 4
36940 | 904C | Pack_RT_SN5 | U16 |  |  |  |  | R | Device serial number 5
36941 | 904D | Pack_RT_SN6 | U16 |  |  |  |  | R | Device serial number 6
36942 | 904E | Pack_RT_SN7 | U16 |  |  |  |  | R | Device serial number 7
36943 | 904F | Pack_RT_SN8 | U16 |  |  |  |  | R | Device serial number 8
36944 | 9050 | Pack_RT_SN9 | U16 |  |  |  |  | R | Device serial number 9
36945 | 9051 | Pack_RT_Cell_Voltage1 | U16 | 0.001 | V |  |  | R | Cell 1 voltage
36946 | 9052 | Pack_RT_Cell_Voltage2 | U16 | 0.001 | V |  |  | R | Cell 2 voltage
36947 | 9053 | Pack_RT_Cell_Voltage3 | U16 | 0.001 | V |  |  | R | Cell 3 voltage
36948 | 9054 | Pack_RT_Cell_Voltage4 | U16 | 0.001 | V |  |  | R | Cell 4 voltage
36949 | 9055 | Pack_RT_Cell_Voltage5 | U16 | 0.001 | V |  |  | R | Cell 5 voltage
36950 | 9056 | Pack_RT_Cell_Voltage6 | U16 | 0.001 | V |  |  | R | Cell 6 voltage
36951 | 9057 | Pack_RT_Cell_Voltage7 | U16 | 0.001 | V |  |  | R | Cell 7 voltage
36952 | 9058 | Pack_RT_Cell_Voltage8 | U16 | 0.001 | V |  |  | R | Cell 8 voltage
36953 | 9059 | Pack_RT_Cell_Voltage9 | U16 | 0.001 | V |  |  | R | Cell 9 voltage
36954 | 905A | Pack_RT_Cell_Voltage10 | U16 | 0.001 | V |  |  | R | Cell 10 voltage
36955 | 905B | Pack_RT_Cell_Voltage11 | U16 | 0.001 | V |  |  | R | Cell 11 voltage
36956 | 905C | Pack_RT_Cell_Voltage12 | U16 | 0.001 | V |  |  | R | Cell 12 voltage
36957 | 905D | Pack_RT_Cell_Voltage13 | U16 | 0.001 | V |  |  | R | Cell 13 voltage
36958 | 905E | Pack_RT_Cell_Voltage14 | U16 | 0.001 | V |  |  | R | Cell 14 voltage
36959 | 905F | Pack_RT_Cell_Voltage15 | U16 | 0.001 | V |  |  | R | Cell 15 voltage
36960 | 9060 | Pack_RT_Cell_Voltage16 | U16 | 0.001 | V |  |  | R | Cell 16 voltage
36961 | 9061 | Pack_RT_Cell_Voltage17 | U16 | 0.001 | V |  |  | R | Cell 17 voltage
36962 | 9062 | Pack_RT_Cell_Voltage18 | U16 | 0.001 | V |  |  | R | Cell 18 voltage
36963 | 9063 | Pack_RT_Cell_Voltage19 | U16 | 0.001 | V |  |  | R | Cell 19 voltage
36964 | 9064 | Pack_RT_Cell_Voltage20 | U16 | 0.001 | V |  |  | R | Cell 20 voltage
36965 | 9065 | Pack_RT_Cell_Voltage21 | U16 | 0.001 | V |  |  | R | Cell 21 voltage
36966 | 9066 | Pack_RT_Cell_Voltage22 | U16 | 0.001 | V |  |  | R | Battery 22 voltage
36967 | 9067 | Pack_RT_Cell_Voltage23 | U16 | 0.001 | V |  |  | R | Battery 23 voltage
36968 | 9068 | Pack_RT_Cell_Voltage24 | U16 | 0.001 | V |  |  | R | Cell 24 voltage
36969 | 9069 | Pack_RT_Cell_Max_Voltage | U16 | 0.001 | V |  |  | R | The highest voltage of the battery
36970 | 906A | Pack_RT_Cell_Min_Voltage | U16 | 0.001 | V |  |  | R | Minimum battery voltage
36971 | 906B | Pack_RT_Temperature1_Pack | I16 | 0.1 | ℃ |  |  | R | Battery pack temperature 1
36972 | 906C | Pack_RT_Temperature2_Pack | I16 | 0.1 | ℃ |  |  | R | Battery pack temperature 2
36973 | 906D | Pack_RT_Temperature3_Pack | I16 | 0.1 | ℃ |  |  | R | Battery pack temperature 3
36974 | 906E | Pack_RT_Temperature4_Pack | I16 | 0.1 | ℃ |  |  | R | Battery pack temperature 4
36975 | 906F | Pack_RT_Temperature_MOS | I16 | 0.1 | ℃ |  |  | R | MOS tube temperature
36976 | 9070 | Pack_RT_Temperature_Env | I16 | 0.1 | ℃ |  |  | R | Ambient temperature in the battery pack
36977 | 9071 | Pack_RT_Current | I16 | 0.1 | A |  |  | R | Battery pack current
36978 | 9072 | Pack_RT_Remaining_Capacity | U16 | 0.1 | Ah |  |  | R | The remaining capacity
36979 | 9073 | Pack_RT_FullCharge_Capacity | U16 | 0.1 | Ah |  |  | R | Full charge capacity
36980 | 9074 | Pack_RT_Cycles | U16 | 1 | times |  |  | R | Cycles
36981 | 9075 | Pack_RT_Balance_State | U16 |  |  |  |  | R | Equilibrium
36982 | 9076 | Pack_RT_Alarm_State | U16 |  |  |  |  | R | Alarm status
36983 | 9077 | Pack_RT_Protect_State | U16 |  |  |  |  | R | Protection status
36984 | 9078 | Pack_RT_Fault_State | U16 |  |  |  |  | R | Fault state
36985 | 9079 | Pack_RT_Total_Voltage | U16 | 0.01 | V |  |  | R | Total Voltage
36986 | 907A | Pack_RT_SOC | U16 | 1 | % |  |  | R | SOC
36987 | 907B
36988 | 907C
36989 | 907D
36990 | 907E
36991 | 907F
36992 | 9080 | AddressMask_BMS3_Fault | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid
36993 | 9081
36994 | 9082
36995 | 9083
36996 | 9084 | Pack_Fault_ID | U16 |  |  |  |  | R | Real-time faulty battery pack number. Bit0-7: The serial number of the battery pack to be queried, the valid range is 0~15, and 0 means the first battery pack Bit8-11: The serial number of the battery pack to be queried, the valid range is 0~15, and 0 means the first battery pack Bit12-15: The serial number of the queried fault, the valid range is 0~5, 0 means the most recent fault
36997 | 9085 | Pack_Fault_Timestamp | U32 |  |  |  |  | R | Fault data timestamp
36998 | 9086
36999 | 9087 | Pack_Fault_SN0 | U16 |  |  |  |  | R | Device serial number 0
37000 | 9088 | Pack_Fault_SN1 | U16 |  |  |  |  | R | Device serial number 1
37001 | 9089 | Pack_Fault_SN2 | U16 |  |  |  |  | R | Device serial number 2
37002 | 908A | Pack_Fault_SN3 | U16 |  |  |  |  | R | Device serial number 3
37003 | 908B | Pack_Fault_SN4 | U16 |  |  |  |  | R | Device serial number 4
37004 | 908C | Pack_Fault_SN5 | U16 |  |  |  |  | R | Device serial number 5
37005 | 908D | Pack_Fault_SN6 | U16 |  |  |  |  | R | Device serial number 6
37006 | 908E | Pack_Fault_SN7 | U16 |  |  |  |  | R | Device serial number 7
37007 | 908F | Pack_Fault_SN8 | U16 |  |  |  |  | R | Device serial number 8
37008 | 9090 | Pack_Fault_SN9 | U16 |  |  |  |  | R | Device serial number 9
37009 | 9091 | Pack_Fault_Cell_Voltage1 | U16 | 0.001 | V |  |  | R | Cell 1 voltage
37010 | 9092 | Pack_Fault_Cell_Voltage2 | U16 | 0.001 | V |  |  | R | Cell 2 voltage
37011 | 9093 | Pack_Fault_Cell_Voltage3 | U16 | 0.001 | V |  |  | R | Cell 3 voltage
37012 | 9094 | Pack_Fault_Cell_Voltage4 | U16 | 0.001 | V |  |  | R | Cell 4 voltage
37013 | 9095 | Pack_Fault_Cell_Voltage5 | U16 | 0.001 | V |  |  | R | Cell 5 voltage
37014 | 9096 | Pack_Fault_Cell_Voltage6 | U16 | 0.001 | V |  |  | R | Cell 6 voltage
37015 | 9097 | Pack_Fault_Cell_Voltage7 | U16 | 0.001 | V |  |  | R | Cell 7 voltage
37016 | 9098 | Pack_Fault_Cell_Voltage8 | U16 | 0.001 | V |  |  | R | Cell 8 voltage
37017 | 9099 | Pack_Fault_Cell_Voltage9 | U16 | 0.001 | V |  |  | R | Cell 9 voltage
37018 | 909A | Pack_Fault_Cell_Voltage10 | U16 | 0.001 | V |  |  | R | Cell 10 voltage
37019 | 909B | Pack_Fault_Cell_Voltage11 | U16 | 0.001 | V |  |  | R | Cell 11 voltage
37020 | 909C | Pack_Fault_Cell_Voltage12 | U16 | 0.001 | V |  |  | R | Cell 12 voltage
37021 | 909D | Pack_Fault_Cell_Voltage13 | U16 | 0.001 | V |  |  | R | Cell 13 voltage
37022 | 909E | Pack_Fault_Cell_Voltage14 | U16 | 0.001 | V |  |  | R | Cell 14 voltage
37023 | 909F | Pack_Fault_Cell_Voltage15 | U16 | 0.001 | V |  |  | R | Cell 15 voltage
37024 | 90A0 | Pack_Fault_Cell_Voltage16 | U16 | 0.001 | V |  |  | R | Cell 16 voltage
37025 | 90A1 | Pack_Fault_Cell_Voltage17 | U16 | 0.001 | V |  |  | R | Cell 17 voltage
37026 | 90A2 | Pack_Fault_Cell_Voltage18 | U16 | 0.001 | V |  |  | R | Cell 18 voltage
37027 | 90A3 | Pack_Fault_Cell_Voltage19 | U16 | 0.001 | V |  |  | R | Cell 19 voltage
37028 | 90A4 | Pack_Fault_Cell_Voltage20 | U16 | 0.001 | V |  |  | R | Cell 20 voltage
37029 | 90A5 | Pack_Fault_Cell_Voltage21 | U16 | 0.001 | V |  |  | R | Cell 21 voltage
37030 | 90A6 | Pack_Fault_Cell_Voltage22 | U16 | 0.001 | V |  |  | R | Battery 22 voltage
37031 | 90A7 | Pack_Fault_Cell_Voltage23 | U16 | 0.001 | V |  |  | R | Battery 23 voltage
37032 | 90A8 | Pack_Fault_Cell_Voltage24 | U16 | 0.001 | V |  |  | R | Cell 24 voltage
37033 | 90A9 | Pack_Fault_Cell_Max_Voltage | U16 | 0.001 | V |  |  | R | The highest voltage of the battery
37034 | 90AA | Pack_Fault_Cell_Min_Voltage | U16 | 0.001 | V |  |  | R | Minimum battery voltage
37035 | 90AB | Pack_Fault_Temperature1_Pack | I16 | 0.1 | ℃ |  |  | R | Battery pack temperature 1
37036 | 90AC | Pack_Fault_Temperature2_Pack | I16 | 0.1 | ℃ |  |  | R | Battery pack temperature 2
37037 | 90AD | Pack_Fault_Temperature3_Pack | I16 | 0.1 | ℃ |  |  | R | Battery pack temperature 3
37038 | 90AE | Pack_Fault_Temperature4_Pack | I16 | 0.1 | ℃ |  |  | R | Battery pack temperature 4
37039 | 90AF | Pack_Fault_Temperature_MOS | I16 | 0.1 | ℃ |  |  | R | MOS tube temperature
37040 | 90B0 | Pack_Fault_Temperature_Env | I16 | 0.1 | ℃ |  |  | R | Ambient temperature in the battery pack
37041 | 90B1 | Pack_Fault_Current | I16 | 0.1 | A |  |  | R | Battery pack current
37042 | 90B2 | Pack_Fault_Remaining_Capacity | U16 | 0.1 | Ah |  |  | R | The remaining capacity
37043 | 90B3 | Pack_Fault_FullCharge_Capacity | U16 | 0.1 | Ah |  |  | R | Full charge capacity
37044 | 90B4 | Pack_Fault_Total_Voltage | U16 | 0.01 | V |  |  | R | Total voltage
37045 | 90B5 | Pack_Alarm_State | U16 |  |  |  |  | R | Alarm status
37046 | 90B6 | Pack_Protect_State | U16 |  |  |  |  | R | Protection status
37047 | 90B7 | Pack_Fault_State | U16 |  |  |  |  | R | Fault state
37048 | 90B8
37049 | 90B9
37050 | 90BA
37051 | 90BB
37052 | 90BC
37053 | 90BD
37054 | 90BE
37055 | 90BF
Note on G1142: PF1VK175: -10000~-8000对应功率因数-1~-0.8
Note on H1142: PF1VK175: 8000~10000对应功率因数0.8~1

## Fault Addresses
Table | Byte | Bit | Field | No. | Remarks | Warning source | classification
Fault1 | byte 0 | bit 0 | GridOVP | 001 | Grid over-voltage | DSPM | Grid
|  | bit 1 | GridUVP | 002 | Grid undervoltage | DSPM
|  | bit 2 | GridOFP | 003 | Grid Overfrequency | DSPM
|  | bit 3 | GridUFP | 004 | Grid Underfrequency | DSPM
|  | bit 4 | GFCI | 005 | Leakage current fault | DSPM&S
|  | bit 5 | OVRT | 006 | High penetration error | DSPM
|  | bit 6 | LVRT | 007 | Low penetration error | DSPM
|  | bit 7 | IslandFault | 008 | Islanding error | DSPM
| byte 1 | bit 0 | GridOVPInstant1 | 009 | Grid voltage transient value overvoltage 1 | DSPM
|  | bit 1 | GridOVPInstant2 | 010 | Grid voltage transient value overvoltage 2 | DSPM
|  | bit 2 | VGridLineFault | 011 | Grid line voltage error | DSPM
|  | bit 3 | InvVoltFault | 012 | Inverter voltage error | DSPM
|  | bit 4 | RefluxFault | 013 | Anti-backflow overload | DSPM&S
|  | bit 5 |  | 014
|  | bit 6 |  | 015
|  | bit 7 |  | 016
Fault2 | byte 0 | bit 0 | HwADErrIGrid | 017 | Grid current sampling error | DSPM | Sampling error
|  | bit 1 | HwADErrDCI(AC) | 018 | Grid current DC component sampling error (AC side) | DSPM
|  | bit 2 | HwADErrVGrid(DC) | 019 | Grid voltage sampling error (DC side) | DSPS
|  | bit 3 | HwADErrVGrid(AC) | 020 | Grid voltage sampling error (AC side) | DSPM
|  | bit 4 | HwGFCIFault(DC) | 021 | Leakage current sampling error (DC side) | DSPS
|  | bit 5 | HwGFCIFault(AC) | 022 | Leakage current sampling error (AC side) | DSPM
|  | bit 6 | HwADErrDCV | 023 | Load voltage DC component sampling error | DSPM
|  | bit 7 | HwADErrIdc | 024 | DC input current sampling error | DSPS
| byte 1 | bit 0 | HwADErrDCI(DC) | 025 | DC component sampling error of grid current (DC side) | DSPS
|  | bit 1 | HwADErrIdcBranch | 026 | DC input branch current sampling error | DSPS
|  | bit 2 |  | 027
|  | bit 3 |  | 028
|  | bit 4 | ConsistentGFCI | 029 | Leakage current consistency error | DSPS
|  | bit 5 | ConsistentVgrid | 030 | Grid voltage consistency error | DSPS
|  | bit 6 | ConsistentDCI | 031 | DCI consistency error | DSPS
|  | bit 7 |  | 032
Fault3 | byte 0 | bit 0 | SpiCommFault(DC) | 033 | SPI communication error (DC side)
|  | bit 1 | SpiCommFault(AC) | 034 | SPI communication error (AC side)
|  | bit 2 | SChip_Fault | 035 | Chip error (DC side)
|  | bit 3 | MChip_Fault | 036 | Chip error (AC side)
|  | bit 4 | HwAuxPowerFault | 037 | Auxiliary power error
|  | bit 5 | InvSoftStartFail | 038 | Inverter soft start failure | DSPM
|  | bit 6 |  | 039
|  | bit 7 |  | 040
| byte 1 | bit 0 | RelayFail | 041 | Relay detection failure | DSPM | System
|  | bit 1 | IsoFault | 042 | Low insulation impedance | DSPS
|  | bit 2 | PEConnectFault | 043 | Grounding error | DSPS
|  | bit 3 | PvConfigError | 044 | Input mode setting error | DSPS
|  | bit 4 | CTDisconnect | 045 | CT error | DSPM&S
|  | bit 5 | ReversalConnect | 046 | Input reversal error | DSPS
|  | bit 6 | ParallelFault | 047 | Parallel error | DSPM
|  | bit 7 | SNTypeFault | 048 | Serial number error | DSPM&S
Fault4 | byte 0 | bit 0 | TempErrBat | 049 | Battery temperature protection | DSPM&S | Temperature
|  | bit 1 | TempErrHeatSink1 | 050 | Heat sink 1 temperature protection | DSPM&S
|  | bit 2 | TempErrHeatSink2 | 051 | Heater 2 temperature protection | DSPM&S
|  | bit 3 | TempErrHeatSink3 | 052 | Heater 3 temperature protection | DSPM&S
|  | bit 4 | TempErrHeatSink4 | 053 | Heatsink 4 temperature protection | DSPM&S
|  | bit 5 | TempErrHeatSink5 | 054 | Heatsink 5 temperature protection | DSPM&S
|  | bit 6 | TempErrHeatSink6 | 055 | Radiator 6 temperature protection | DSPM&S
|  | bit 7 |  | 056
| byte 1 | bit 0 | TempErrEnv1 | 057 | Ambient temperature 1 protection | DSPM&S
|  | bit 1 | TempErrEnv2 | 058 | Ambient temperature 2 protection | DSPM&S
|  | bit 2 | TempErrInv1 | 059 | Module 1 temperature protection | DSPM&S
|  | bit 3 | TempErrInv2 | 060 | Module 2 temperature protection | DSPM&S
|  | bit 4 | TempErrInv3 | 061 | Module 3 temperature protection | DSPM&S
|  | bit 5 | TempDiffErrInv | 062 | Module temperature difference is too large | DSPM&S
|  | bit 6 |  | 063
|  | bit 7 |  | 064
Fault5 | byte 0 | bit 0 | BusRmsUnbalance | 065 | Bus voltage RMS unbalance | DSPM | Over and under voltage
|  | bit 1 | BusInstUnbalance | 066 | Bus voltage transient value unbalance | DSPM
|  | bit 2 | BusUVP | 067 | Undervoltage of busbar during grid connection | DSPM
|  | bit 3 | BusZVP | 068 | Bus bar low voltage | DSPM
|  | bit 4 | PVOVP | 069 | PV overvoltage | DSPS
|  | bit 5 | BatOVP | 070 | Battery over-voltage | DSPS
|  | bit 6 | LLCBusOVP | 071 | LLCBus overvoltage protection | DSPS
|  | bit 7 | SwBusRmsOVP | 072 | Inverter bus voltage RMS software overvoltage | DSPM
| byte 1 | bit 0 | SwBusIOVP | 073 | Inverter bus voltage transient value software overvoltage | DSPM
|  | bit 1 | FlyingCapOVP | 074 | Flying Cross Capacitor Overvoltage Protection | DSPM&S
|  | bit 2 | FlyingCapUVP | 075 | Flying Cross capacitor undervoltage protection | DSPM&S
|  | bit 3 |  | 076
|  | bit 4 |  | 077
|  | bit 5 |  | 078
|  | bit 6 |  | 079
|  | bit 7 |  | 080
Fault6 | byte 0 | bit 0 | SwBatOCP | 081 | Battery overcurrent software protection | DSPS | Current
|  | bit 1 | DciOCP | 082 | Dci overcurrent protection | DSPM
|  | bit 2 | SwIOCP | 083 | Output transient current protection | DSPM
|  | bit 3 | SwBuckBoostOCP | 084 | BuckBoost software overcurrent | DSPS
|  | bit 4 | SwAcRmsOCP | 085 | Output RMS current protection | DSPM
|  | bit 5 | SwPvOCPInstant | 086 | PV instantaneous current overcurrent software protection | DSPS
|  | bit 6 | IpvUnbalance | 087 | PV parallel uneven current | DSPS
|  | bit 7 | IacUnbalance | 088 | Output current unbalance | DSPM
| byte 1 | bit 0 | SwPvOCP | 089 | PV software overcurrent protection | DSPM&S
|  | bit 1 | IbalanceOCP | 090 | Balanced circuit overcurrent protection | DSPM&S
|  | bit 2 | ResOver | 091 | Resonance protection | DSPM
|  | bit 3 |  | 092
|  | bit 4 |  | 093
|  | bit 5 |  | 094
|  | bit 6 |  | 095
|  | bit 7 |  | 096
Fault7 | byte 0 | bit 0 | HwLLCBusOVP | 097 | LLC bus hardware overvoltage | DSPS | Hardware signal
|  | bit 1 | HwBusOVP | 098 | Inverter bus hardware overvoltage | DSPM
|  | bit 2 | HwBuckBoostOCP | 099 | BuckBoost hardware overcurrent | DSPS
|  | bit 3 | HwBatOCP | 100 | Battery hardware overcurrent | DSPS
|  | bit 4 |  | 101
|  | bit 5 | HwPVOCP | 102 | PV hardware overcurrent | DSPS
|  | bit 6 | HwACOCP | 103 | AC output hardware overcurrent | DSPM
|  | bit 7 |  | 104
| byte 1 | bit 0 | MeterCommFault | 105 | Power meter error | DSPM&S | Hardware signal reservation, overload
|  | bit 1 | SNMachineFault | 106 | Serial number model error
|  | bit 2 |  | 107
|  | bit 3 |  | 108
|  | bit 4 |  | 109
|  | bit 5 | Overload1 | 110 | Overload protection 1 | DSPM
|  | bit 6 | Overload2 | 111 | Overload protection 2 | DSPM
|  | bit 7 | Overload3 | 112 | Overload protection 3 | DSPM
Fault8 | byte 0 | bit 0 | OverTempDerating | 113 | Overtemperature derating | DSPM | Load reduction | This fault word is only used to generate an alarm and will not directly cause the system to enter a fault state.
|  | bit 1 | FreqDerating | 114 | Frequency down load | DSPM
|  | bit 2 | FreqLoading | 115 | Frequency loading | DSPM
|  | bit 3 | VoltDerating | 116 | Voltage down load | DSPM
|  | bit 4 | VoltLoading | 117 | Voltage loading | DSPM
|  | bit 5 |  | 118 |  | DSPM
|  | bit 6 |  | 119
|  | bit 7 |  | 120
| byte 1 | bit 0 | SpdFail(DC) | 121 | Lightning protection failure (DC) |  | Shut down
|  | bit 1 | SpdFail(AC) | 122 | Lightning protection failure (AC)
|  | bit 2 |  | 123
|  | bit 3 | BatDchgProhibit | 124 | Battery low voltage protection
|  | bit 4 | BatLowVoltShut | 125 | Battery low voltage shutdown
|  | bit 5 |  | 126 | Battery low voltage pre-alarm
|  | bit 6 |  | 127
|  | bit 7 |  | 128
Fault9 | byte 0 | bit 0 | PermHwAcOCP | 129 | Output hardware overcurrent permanent fault | DSPM | Permanent
|  | bit 1 | PermBusOVP | 130 | Bus overvoltage permanent fault | DSPM
|  | bit 2 | PermHwBusOVP | 131 | Bus hardware over-voltage permanent fault | DSPM
|  | bit 3 | PermIpvUnbalance | 132 | PV uneven flow permanent fault | DSPS
|  | bit 4 | PermEPSBatOCP | 133 | Battery overcurrent permanent fault in EPS mode | DSPM
|  | bit 5 | PermAcOCPInstant | 134 | Output transient overcurrent permanent fault | DSPM
|  | bit 6 | PermIacUnbalance | 135 | Output current unbalance permanent fault | DSPM
|  | bit 7 |  | 136
| byte 1 | bit 0 | PermInCfgError | 137 | Input mode setting error permanent fault | DSPS
|  | bit 1 | PermDCOCPInstant | 138 | Input overcurrent permanent fault | DSPS
|  | bit 2 | PermHwDCOCP | 139 | Input hardware overcurrent permanent fault | DSPS
|  | bit 3 | PermRelayFail | 140 | Relay permanent fault | DSPM
|  | bit 4 | PermBusUnbalance | 141 | Bus unbalance permanent fault | DSPM
|  | bit 5 | PermSpdFail(DC) | 142 | Lightning protection permanent fault - DC side | DSPS
|  | bit 6 | PermSpdFail(AC) | 143 | Lightning protection permanent fault - AC side | DSPM
|  | bit 7 |  | 144
Fault10 | byte 0 | bit 0 | USBFault | 145 | USB fault | ARM | Communication board
|  | bit 1 | WifiFault | 146 | WIFI fault | ARM
|  | bit 2 | BluetoothFault | 147 | Bluetooth fault | ARM
|  | bit 3 | RTCFault | 148 | RTC clock fault | ARM
|  | bit 4 | CommEEPROMFault | 149 | Communication board EEPROM error | ARM
|  | bit 5 | FlashFault | 150 | Communication board FLASH error | ARM
|  | bit 6 |  | 151
|  | bit 7 | SafetyVerFault | 152 | Safety regulation version error | ARM
| byte 1 | bit 0 | SCILose(DC) | 153 | SCI communication error (DC side) | ARM
|  | bit 1 | SCILose(AC) | 154 | SCI communication error (AC side) | ARM
|  | bit 2 | SCILose(Fuse) | 155 | SCI communication error (convergence board side) | ARM
|  | bit 3 | SoftVerError | 156 | Software version inconsistency | ARM
|  | bit 4 | BMS1CommFault | 157 | Lithium battery 1 communication error | ARM
|  | bit 5 | BMS2CommFault | 158 | Li-ion battery 2 communication error
|  | bit 6 | BMS3CommFault | 159 | Lithium battery 3 communication error
|  | bit 7 | BMS4CommFault | 160 | Lithium battery 4 communication failure
Fault11 | byte 0 | bit 0 | ForceShutdown | 161 | Forced shutdown | ARM | The communication board is shut down and the load is reduced
|  | bit 1 | RemoteShutdown | 162 | Remote shutdown | ARM
|  | bit 2 | Drms0Shutdown | 163 | Drms0 shutdown | ARM
|  | bit 3 |  | 164
|  | bit 4 | RemoteDerating | 165 | Remote down load | ARM
|  | bit 5 | LogicIfDerating | 166 | Logic interface down load | ARM
|  | bit 6 | AlarmAntiReflux | 167 | Anti-Reverse Flow Downgrade | ARM
|  | bit 7 |  | 168
| byte 1 | bit 0 | FanFault1 | 169 | Fan 1 failure | ARM | External components
|  | bit 1 | FanFault2 | 170 | Fan 2 failure | ARM
|  | bit 2 | FanFault3 | 171 | Fan 3 failure | ARM
|  | bit 3 | FanFault4 | 172 | Fan 4 failure | ARM
|  | bit 4 | FanFault5 | 173 | Fan 5 failure | ARM
|  | bit 5 | FanFault6 | 174 | Fan 6 failure | ARM
|  | bit 6 | FanFault7 | 175 | Fan 7 fault | ARM
|  | bit 7 | MeterCommLose | 176 | Meter communication failure | ARM
Fault12 | byte 0 | bit 0 | BMS OVP | 177 | BMS over-voltage alarm | BMS | BMS
|  | bit 1 | BMS UVP | 178 | BMS undervoltage alarm | BMS
|  | bit 2 | BMS OTP | 179 | BMS high temperature alarm | BMS
|  | bit 3 | BMS UTP | 180 | BMS low temperature alarm | BMS
|  | bit 4 | BMS OCP | 181 | BMS charge/discharge overload alarm | BMS
|  | bit 5 | BMS Short | 182 | BMS short circuit alarm | BMS
|  | bit 6 | BMS VerFault | 183 | BMS version inconsistency | ARM
|  | bit 7 | BMS CAN VerFault | 184 | BMS CAN version inconsistency | ARM
| byte 1 | bit 0 | BMS CAN VerLow | 185 | BMS CAN version is too low | ARM
|  | bit 1 |  | 186
|  | bit 2 |  | 187
|  | bit 3 |  | 188
|  | bit 4 | AFCICommLose | 189 | Arc device communication failure | ARM
|  | bit 5 | DCArcingAlarm | 190 | DC arc alarm fault | ARM
|  | bit 6 | PID_Output_Fail | 191 | PID repair failed | ARM
|  | bit 7 | PLC_Com_Fail | 192 | PLC module heartbeat loss
Fault13 | byte 0 | bit 0 | StrFuseALM1-1 | 193 | String fuse open circuit alarm 1-1 | FUSE | FUSE
|  | bit 1 | StrFuseALM1-2 | 194 | String fuse open circuit alarm 1-2 | FUSE
|  | bit 2 | StrFuseALM2-1 | 195 | String fuse open circuit alarm 2-1 | FUSE
|  | bit 3 | StrFuseALM2-2 | 196 | String fuse open circuit alarm 2-2 | FUSE
|  | bit 4 | StrFuseALM3-1 | 197 | String fuse open circuit alarm 3-1 | FUSE
|  | bit 5 | StrFuseALM3-2 | 198 | String fuse open circuit alarm 3-2 | FUSE
|  | bit 6 | StrFuseALM4-1 | 199 | String fuse open circuit alarm 4-1 | FUSE
|  | bit 7 | StrFuseALM4-2 | 200 | String fuse open circuit alarm 4-2 | FUSE
| byte 1 | bit 0 | StrFuseALM5-1 | 201 | String fuse open circuit alarm 5-1 | FUSE
|  | bit 1 | StrFuseALM5-2 | 202 | String fuse open circuit alarm 5-2 | FUSE
|  | bit 2 | StrFuseALM6-1 | 203 | String fuse open circuit alarm 6-1 | FUSE
|  | bit 3 | StrFuseALM6-2 | 204 | String fuse open circuit alarm 6-2 | FUSE
|  | bit 4 | StrFuseALM7-1 | 205 | String fuse open circuit alarm 7-1 | FUSE
|  | bit 5 | StrFuseALM7-2 | 206 | String fuse open circuit alarm 7-2 | FUSE
|  | bit 6 | StrFuseALM8-1 | 207 | String fuse open circuit alarm 8-1 | FUSE
|  | bit 7 | StrFuseALM8-2 | 208 | String fuse open circuit alarm 8-2 | FUSE
Fault14 | byte 0 | bit 0 | StrFuseALM9-1 | 209 | String fuse open circuit alarm 9-1 | FUSE
|  | bit 1 | StrFuseALM9-2 | 210 | String fuse open circuit alarm 9-2 | FUSE
|  | bit 2 | StrFuseALM10-1 | 211 | String fuse open circuit alarm 10-1 | FUSE
|  | bit 3 | StrFuseALM10-2 | 212 | String fuse open circuit alarm 10-2 | FUSE
|  | bit 4 | StrFuseALM11-1 | 213 | String fuse open circuit alarm 11-1 | FUSE
|  | bit 5 | StrFuseALM11-2 | 214 | String fuse open circuit alarm 11-2 | FUSE
|  | bit 6 | StrFuseALM12-1 | 215 | String fuse open circuit alarm 12-1 | FUSE
|  | bit 7 | StrFuseALM12-2 | 216 | String fuse open circuit alarm 12-2 | FUSE
| byte 1 | bit 0 | StrFuseALM13-1 | 217 | String fuse open circuit alarm 13-1 | FUSE
|  | bit 1 | StrFuseALM13-2 | 218 | String fuse open circuit alarm 13-2 | FUSE
|  | bit 2 | StrFuseALM14-1 | 219 | String fuse open circuit alarm 14-1 | FUSE
|  | bit 3 | StrFuseALM14-2 | 220 | String fuse open circuit alarm 14-2 | FUSE
|  | bit 4 | StrFuseALM15-1 | 221 | String fuse open circuit alarm 15-1 | FUSE
|  | bit 5 | StrFuseALM15-2 | 222 | String fuse open circuit alarm 15-2 | FUSE
|  | bit 6 | StrFuseALM16-1 | 223 | String fuse open circuit alarm 16-1 | FUSE
|  | bit 7 | StrFuseALM16-2 | 224 | String fuse open circuit alarm 16-2 | FUSE
Fault15 | byte 0 | bit 0 | InputFuseALM0 | 225 | Battery input fuse open circuit alarm 0 | FUSE
|  | bit 1 | InputFuseALM1 | 226 | Battery input fuse open circuit alarm 1 | FUSE
|  | bit 2 | InputFuseALM2 | 227 | Battery input fuse open circuit alarm 2 | FUSE
|  | bit 3 | InputFuseALM3 | 228 | Battery input fuse open circuit alarm 3 | FUSE
|  | bit 4 | InputFuseALM4 | 229 | Battery input fuse open circuit alarm 4 | FUSE
|  | bit 5 | InputFuseALM5 | 230 | Battery input fuse open circuit alarm 5 | FUSE
|  | bit 6 | InputFuseALM6 | 231 | Battery input fuse open circuit alarm 6 | FUSE
|  | bit 7 | InputFuseALM7 | 232 | Battery input fuse open circuit alarm 7 | FUSE
| byte 1 | bit 0 | InputFuseALM8 | 233 | Battery input fuse open circuit alarm 8 | FUSE
|  | bit 1 | InputFuseALM9 | 234 | Battery input fuse open circuit alarm 9 | FUSE
|  | bit 2 | InputFuseALM10 | 235 | Battery input fuse open circuit alarm 10 | FUSE
|  | bit 3 | InputFuseALM11 | 236 | Battery input fuse open circuit alarm 11 | FUSE
|  | bit 4 | InputFuseALM12 | 237 | Battery input fuse open circuit alarm 12 | FUSE
|  | bit 5 | InputFuseALM13 | 238 | Battery input fuse open circuit alarm 13 | FUSE
|  | bit 6 | InputFuseALM14 | 239 | Battery input fuse open circuit alarm 14 | FUSE
|  | bit 7 | InputFuseALM15 | 240 | Battery input fuse open circuit alarm 15 | FUSE
Fault16 | byte 0 | bit 0 | CombinerOVGp1 | 241 |  |  | Confluence
|  | bit 1 | CombinerOVGp2 | 242
|  | bit 2 | CombinerOVGp3 | 243
|  | bit 3 | CombinerOVGp4 | 244
|  | bit 4 | CombinerOVGp5 | 245
|  | bit 5 | CombinerOVGp6 | 246
|  | bit 6 | CombinerOVGp7 | 247
|  | bit 7 | CombinerOVGp8 | 248
| byte 1 | bit 0 | CombinerOVGp9 | 249
|  | bit 1 | CombinerOVGp10 | 250
|  | bit 2 | CombinerOVGp11 | 251
|  | bit 3 | CombinerOVGp12 | 252
|  | bit 4 | CombinerOVGp13 | 253
|  | bit 5 | CombinerOVGp14 | 254
|  | bit 6 | CombinerOVGp15 | 255
|  | bit 7 | CombinerOVGp16 | 256
Fault17 | byte 0 | bit 0 | CombinerUVGp1 | 257 |  |  | Confluence
|  | bit 1 | CombinerUVGp2 | 258
|  | bit 2 | CombinerUVGp3 | 259
|  | bit 3 | CombinerUVGp4 | 260
|  | bit 4 | CombinerUVGp5 | 261
|  | bit 5 | CombinerUVGp6 | 262
|  | bit 6 | CombinerUVGp7 | 263
|  | bit 7 | CombinerUVGp8 | 264
| byte 1 | bit 0 | CombinerUVGp9 | 265
|  | bit 1 | CombinerUVGp10 | 266
|  | bit 2 | CombinerUVGp11 | 267
|  | bit 3 | CombinerUVGp12 | 268
|  | bit 4 | CombinerUVGp13 | 269
|  | bit 5 | CombinerUVGp14 | 270
|  | bit 6 | CombinerUVGp15 | 271
|  | bit 7 | CombinerUVGp16 | 272
Fault18 | byte 0 | bit 0 | CombinerOC1 | 273 |  |  | Confluence
|  | bit 1 | CombinerOC2 | 274
|  | bit 2 | CombinerOC3 | 275
|  | bit 3 | CombinerOC4 | 276
|  | bit 4 | CombinerOC5 | 277
|  | bit 5 | CombinerOC6 | 278
|  | bit 6 | CombinerOC7 | 279
|  | bit 7 | CombinerOC8 | 280
| byte 1 | bit 0 | CombinerOC9 | 281
|  | bit 1 | CombinerOC10 | 282
|  | bit 2 | CombinerOC11 | 283
|  | bit 3 | CombinerOC12 | 284
|  | bit 4 | CombinerOC13 | 285
|  | bit 5 | CombinerOC14 | 286
|  | bit 6 | CombinerOC15 | 287
|  | bit 7 | CombinerOC16 | 288
Fault19 | byte 0 | bit 0 | CombinerOC17 | 289 |  |  | Confluence
|  | bit 1 | CombinerOC18 | 290
|  | bit 2 | CombinerOC19 | 291
|  | bit 3 | CombinerOC20 | 292
|  | bit 4 | CombinerOC21 | 293
|  | bit 5 | CombinerOC22 | 294
|  | bit 6 | CombinerOC23 | 295
|  | bit 7 | CombinerOC24 | 296
| byte 1 | bit 0 | CombinerOC25 | 297
|  | bit 1 | CombinerOC26 | 298
|  | bit 2 | CombinerOC27 | 299
|  | bit 3 | CombinerOC28 | 300
|  | bit 4 | CombinerOC29 | 301
|  | bit 5 | CombinerOC30 | 302
|  | bit 6 | CombinerOC31 | 303
|  | bit 7 | CombinerOC32 | 304
Fault20 | byte 0 | bit 0 |  | 305 |  |  | Confluence
|  | bit 1 |  | 306
|  | bit 2 |  | 307
|  | bit 3 |  | 308
|  | bit 4 |  | 309
|  | bit 5 |  | 310
|  | bit 6 |  | 311
|  | bit 7 |  | 312
| byte 1 | bit 0 |  | 313
|  | bit 1 |  | 314
|  | bit 2 |  | 315
|  | bit 3 |  | 316
|  | bit 4 |  | 317
|  | bit 5 |  | 318
|  | bit 6 |  | 319
|  | bit 7 |  | 320
Fault21 | byte 0 | bit 0 |  | 321 |  |  | Confluence
|  | bit 1 |  | 322
|  | bit 2 |  | 323
|  | bit 3 |  | 324
|  | bit 4 |  | 325
|  | bit 5 |  | 326
|  | bit 6 |  | 327
|  | bit 7 |  | 328
| byte 1 | bit 0 |  | 329
|  | bit 1 |  | 330
|  | bit 2 |  | 331
|  | bit 3 |  | 332
|  | bit 4 |  | 333
|  | bit 5 |  | 334
|  | bit 6 |  | 335
|  | bit 7 |  | 336
Fault22 | byte 0 | bit 0 | CombinerRefluxFault1 | 337 |  |  | Confluence
|  | bit 1 | CombinerRefluxFault2 | 338
|  | bit 2 | CombinerRefluxFault3 | 339
|  | bit 3 | CombinerRefluxFault4 | 340
|  | bit 4 | CombinerRefluxFault5 | 341
|  | bit 5 | CombinerRefluxFault6 | 342
|  | bit 6 | CombinerRefluxFault7 | 343
|  | bit 7 | CombinerRefluxFault8 | 344
| byte 1 | bit 0 | CombinerRefluxFault9 | 345
|  | bit 1 | CombinerRefluxFault10 | 346
|  | bit 2 | CombinerRefluxFault11 | 347
|  | bit 3 | CombinerRefluxFault12 | 348
|  | bit 4 | CombinerRefluxFault13 | 349
|  | bit 5 | CombinerRefluxFault14 | 350
|  | bit 6 | CombinerRefluxFault15 | 351
|  | bit 7 | CombinerRefluxFault16 | 352
Fault23 | byte 0 | bit 0 | CombinerRefluxFault17 | 353 |  |  | Confluence
|  | bit 1 | CombinerRefluxFault18 | 354
|  | bit 2 | CombinerRefluxFault19 | 355
|  | bit 3 | CombinerRefluxFault20 | 356
|  | bit 4 | CombinerRefluxFault21 | 357
|  | bit 5 | CombinerRefluxFault22 | 358
|  | bit 6 | CombinerRefluxFault23 | 359
|  | bit 7 | CombinerRefluxFault24 | 360
| byte 1 | bit 0 | CombinerRefluxFault25 | 361
|  | bit 1 | CombinerRefluxFault26 | 362
|  | bit 2 | CombinerRefluxFault27 | 363
|  | bit 3 | CombinerRefluxFault28 | 364
|  | bit 4 | CombinerRefluxFault29 | 365
|  | bit 5 | CombinerRefluxFault30 | 366
|  | bit 6 | CombinerRefluxFault31 | 367
|  | bit 7 | CombinerRefluxFault32 | 368
Fault24 | byte 0 | bit 0 |  | 369 |  |  | Confluence
|  | bit 1 |  | 370
|  | bit 2 |  | 371
|  | bit 3 |  | 372
|  | bit 4 |  | 373
|  | bit 5 |  | 374
|  | bit 6 |  | 375
|  | bit 7 |  | 376
| byte 1 | bit 0 |  | 377
|  | bit 1 |  | 378
|  | bit 2 |  | 379
|  | bit 3 |  | 380
|  | bit 4 |  | 381
|  | bit 5 |  | 382
|  | bit 6 |  | 383
|  | bit 7 |  | 384
Fault25 | byte 0 | bit 0 |  | 385 |  |  | Confluence
|  | bit 1 |  | 386
|  | bit 2 |  | 387
|  | bit 3 |  | 388
|  | bit 4 |  | 389
|  | bit 5 |  | 390
|  | bit 6 |  | 391
|  | bit 7 |  | 392
| byte 1 | bit 0 |  | 393
|  | bit 1 |  | 394
|  | bit 2 |  | 395
|  | bit 3 |  | 396
|  | bit 4 |  | 397
|  | bit 5 |  | 398
|  | bit 6 |  | 399
|  | bit 7 |  | 400
Fault26 | byte 0 | bit 0 | AFCI0 | 401 | Arc fault |  | AFCI
|  | bit 1 | AFCI1 | 402 | Arc fault
|  | bit 2 | AFCI2 | 403 | Arc fault
|  | bit 3 | AFCI3 | 404 | Arc fault
|  | bit 4 | AFCI4 | 405 | Arc fault
|  | bit 5 | AFCI5 | 406 | Arc fault
|  | bit 6 | AFCI6 | 407 | Arc fault
|  | bit 7 | AFCI7 | 408 | Arc fault
| byte 1 | bit 0 | AFCI8 | 409 | Arc fault
|  | bit 1 | AFCI9 | 410 | Arc fault
|  | bit 2 | AFCI10 | 411 | Arc fault
|  | bit 3 | AFCI11 | 412 | Arc fault
|  | bit 4 | AFCI12 | 413 | Arc fault
|  | bit 5 | AFCI13 | 414 | Arc fault
|  | bit 6 | AFCI14 | 415 | Arc fault
|  | bit 7 | AFCI15 | 416 | Arc fault
Fault27 | byte 0 | bit 0 | AFCI16 | 417 | Arc fault |  | AFCI
|  | bit 1 | AFCI17 | 418 | Arc fault
|  | bit 2 | AFCI18 | 419 | Arc fault
|  | bit 3 | AFCI19 | 420 | Arc fault
|  | bit 4 | AFCI20 | 421 | Arc fault
|  | bit 5 | AFCI21 | 422 | Arc fault
|  | bit 6 | AFCI22 | 423 | Arc fault
|  | bit 7 | AFCI23 | 424 | Arc fault
| byte 1 | bit 0 | AFCI24 | 425 | Arc fault
|  | bit 1 | AFCI25 | 426 | Arc fault
|  | bit 2 | AFCI26 | 427 | Arc fault
|  | bit 3 | AFCI27 | 428 | Arc fault
|  | bit 4 | AFCI28 | 429 | Arc fault
|  | bit 5 | AFCI29 | 430 | Arc fault
|  | bit 6 | AFCI30 | 431 | Arc fault
|  | bit 7 | AFCI31 | 432 | Arc fault

## Version
Modified date | Address | Modification description
2020-05-23 | 0x0940 | Add Bit4
| 0x0404 | Add 2 new status descriptions
| 0x09C0 | Add Bit3
| 0x09DB-0x09DE | Add parameters
| 0x2006 | Update value definition description
2020-06-03 | 0x102D | Add CT automatic calibration register
2020-06-10 | 0x0940 | Add Bit5
2020-06-29 | 0x0914-0x0915 | Add parameters
| Fault2-byte1-bit6 | Add fault
| Fault3-byte1-bit6 | Add fault
2020-08-31 | 0x1046 | Add battery protocol type
| 0x1038 | Add address
| 0xA07C-0xA07F | Add address
| Fault3-byte0-bit5 | Add InverterSoftStartFail
| Fault3-byte1-bit7 | Add SNTypeFault
| Fault9-byte1-bit5 | Add unrecoverSpdFail(DC)
| Fault9-byte1-bit6 | Add unrecoverSpdFail(AC)
| Fault2-byte0-bit1 | Modify fault name
| Fault2-byte1-bit0 | Add HwADFaultDCI(DC)
| Fault2-byte1-bit1 | Add HwADFaultIdcBranch
| Fault10-byte1-bit4 | Modify fault name
| Fault10-byte1-bit5 | Add BMS2CommunicatonFault
| Fault10-byte1-bit6 | Add BMS3CommunicatonFault
| Fault10-byte1-bit7 | Add BMS4CommunicatonFault
| Fault10-byte0-bit7 | Add SafetyVerFault
2020-09-04 | 0x803C-0x803F | Add address
| 0x9000-0x9FFF | Add BMS transparent transmission area
| 0x06D1-0x06E2 | Add address
| Fault5-byte1-bit1 | Add FlyingCapOVP
2020-10-13 | 0x08C8-0x08CC | Add safety parameters
| 0x0A04-0x0A05 | Add safety parameters
| 0x1050 | Voltage accuracy problem correction
2020-10-30 | 0x9000-0x9FFF | New package ID in the real-time data section of the BMS transparent transmission area
| 0x4B0-0x4B9 | Add address
| 0x522-0x527 | Add address
| Fault11-byte1-bit7 | Add fault
2020-11-16 | 0x1039-0x103D | Add address
2020-12-02 | 0x0901，0x0A03 | Update the value range of the original address
| 0x1046 | Update the value range of the original address
| 0x1052 | Add battery parameter address
| 0x1054-0x1056 | Add battery parameter address
| 0x1023 | Update the value range of the original address
| 0x1024 | Original address unit update
| 0x1084-0x108C | Add arc configuration address
| 0xA070-0xA075 | Add address
| 0x0780-0x07BF | Add arc real-time information area
| 0x2007-0x200B | Add new safety country name address
| 0x0432-0x043A | Add fault information address
| Fault6-byte1-bit0 | Add SwPvOCP
| Fault26/27 | Add AFCI fault
2021-01-27 | 0x9005 | Date register type problem fixed
| 0x9051-0x906A, 0x9079, 0x9091-0x90AA, 0x90B4 | Accuracy change
| 0x907A | Add address
| 0x1105-0x110B | Add address
| 0x04BA-0x04BC | Add address
| 0x108D-0x108E | Add address
| Fault11-byte1-bit6 | Add FanFault7
| Fault12-byte0-bit6 | Add BMS VerFault
| Fault12-byte0-bit7 | Add BMS CAN VerFault
| Fault12-byte1-bit0 | Add BMS CAN VerLow
| Fault12-byte1-bit4 | Add AFCICommLose
| Fault12-byte1-bit5 | Add DCArcingAlarmFault
2021-02-05 | Fault7-byte1-bit0 | Add MeterCommFault
2021-02-16 | 0x118D-0x1190, 0x1197-0x119A, 0x11A1-0x11A4 | Data type update
| 0x1035 | Update the register value range and value definition
| Fault6-byte1-bit1 | Add IbalanceOCP
| 0x1024 | Fix the accuracy problem
2021-03-16 | Fault1-byte1-bit3 | Field name correction
| Fault1-byte1-bit4 | Added anti-backflow overload fault
| Fault8-byte1-bit3 | Field name correction
| 0x460-0x465 | Added safety version number register
| 0x0951-0x0960 | Add new safety parameter address
| 0x0980 | Added bit field definition to the original address
| 0x0981 | Maximum and minimum value corrections, please check the remarks
| 0x0982 | Maximum and minimum value corrections, please check the remarks
| 0x0993 | Update the original address field, unit, and remarks
| 0x0995 | Original address lot, remarks update
| 0x0996 | Update the original address field, type, remarks
| 0x09A1 | New safety parameter address
| 0x09C0 | Added bit field definition to the original address
| 0x0A00 | Added bit field definition to the original address
2021-06-19 | 0x05C4 | Add the total PV power address
| 0x0667-0x0669 | Add battery summary information address
| 0x0916 | Add the voltage drop time address
| 0x0940 | Add Bit6
| 0x0961-0x0962 | Add frequency address of over and under frequency power crossing point
| 0x1060 | Add PCC power acquisition device configuration address
| Fault4-byte1-bit5 | Increase the fault bit
2021-08-03 | 0x1098-0x109C | Add PID configuration address
| 0x110F | Add PID control address
| Fault12-byte1-bit6 | Add fault
2021-08-11 | 0x044C | Change from reserved address to valid serial number address
| 0x0470-0x0476 | Added 2 valid serial number addresses, and 5 reserved addresses
| 0x10A0-0x10A1 | Add PLC enable and configuration address
| 0x10A5-0x10A6 | Added BLE enable and configuration address
| 0x10B0-0x10A4 | Modify PID enable and configuration address
| 0x8027 | Change from reserved address to valid serial number address
| 0x8028-0x802E | Added 2 factory effective serial number addresses, and 5 reserved addresses
| 0x802F-0x8032 | Newly added peripheral configuration address and peripheral configuration BIT correspondence table
| 0xA06A | Add remote reset command
| Fault12-byte1-bit7 | Added PLC heartbeat failure
2021-08-31 | 0x1108 | Change the address data type to signed
| Fault13、Fault14 | Alarm name change
| 0x0040-0x0043 | Add agreement "general" area
| 0x0044 | Add protocol version number
2021-09-06 | Fault8-byte1-bit0 Fault8-byte1-bit1 | Add lightning protection failure (DC) and lightning protection failure (AC)
| 0x0044 | Update protocol version definition
| 0x0045-0x0047 | Add chipset code
2021-10-11 | 0x0940 | Add Bit7 definition
2021-11-03 | 0x1023 | Add mode definition: phase power mode
| 0x1034 | Language definition
| 0x1061 | Add resonance detection sensitivity register
| 0x1110 | Add mode definition: off-grid mode
| 0x1144-0x1146 | Added off-grid mode register
| 0x203D-0x203F | Add target chip definition: PCU (Power Control Unit) and BMS (Battery Management System)
| 0x7000-0x707F | Add ODM data customization area
| ID91 | Add resonance protection ID
| ID106 | Add serial number model error ID